## Projects and Benefits
Projects and Benefits
As of 2026-06-04 09:54:07 Pacific Standard Time/PST • Generated by Daniel Tuhus-Dubrow • Sorted by Project: Project Number (Ascending)
Filtered By
Show: All projects
Project: Project Number |  | Benefit: Benefit Name | Benefit Type | Annual Cost Savings | Electric Savings | District Steam Savings | Fuel Oil Savings | Natural Gas Savings | Propane Savings | Peak Demand Reduction | Project Type | Benefit Narrative
1275 |  | Optimize Seqence | Energy Savings | 11400 | [6 empty] | Retrocommissioning
1275 |  | Function performance testing | Energy Savings | [7 empty] | Retrocommissioning
1275 |  | Sensor calibration | Energy Savings | [7 empty] | Retrocommissioning
1275 |  | Automatic boiler isolation valves (2) | Energy Savings | [7 empty] | Retrocommissioning
1275 |  | 2 way valves (13) | Energy Savings | [7 empty] | Retrocommissioning
1275 |  | HRU VFD (2) | Energy Savings | [7 empty] | Retrocommissioning
1275 |  | Differential pressure sensor (2) | Energy Savings | [7 empty] | Retrocommissioning
1275 |  | Damper Actuator/ control valve repair (14) | Energy Savings | [7 empty] | Retrocommissioning
1275 |  | Guidance RTU-1 controller (1) | Energy Savings | [7 empty] | Retrocommissioning
1275 |  | Tighten Schedules and Setbacks | Energy Savings | 515 | 1270 | [5 empty] | Retrocommissioning | There are occupancy schedules implemented through the BAS to control when equipment starts and stops, and to establish occupied and unoccupied temperature setpoints. Most spaces are in occupied mode from 5:00 a.m. to 3:00 p.m. on weekdays, with occupied a
1275 |  | Optimize control of Bus Engine Block Heater | Energy Savings | 2162 | 24570 | [5 empty] | Retrocommissioning | There are twenty-five (25) 1,500-watt electric block heaters for the school bus engines. It is possible the operation of these heaters can be optimized if they are currently being operated manually (e.g. plugged in at the end of the day and unplugged in t
1275 |  | Add monitoring and Control Capability for Exhaust Fans | Energy Savings | 773 | 1910 | [5 empty] | Retrocommissioning | While most of the equipment in the building is visible and controlled through the building automation system, there are several exhaust fans that are not currently integrated into the system. The building operator expressed interest in adding status and c
1275 |  | Ensure Tight Cosure of Unit Ventilators Outside Air Dampers | Energy Savings | 540 | [6 empty] | Retrocommissioning | Many of the unit ventilators have outside air dampers that do not close tightly, resulting in uncontrolled infiltration of outdoor air when the damper is commanded closed. Consider incorporating adjustment of outside air dampers as part of routine mainten
1275 |  | Raise Unit Ventilator Supply Air Tempeature Setpoints | Energy Savings | 56 | 640 | [5 empty] | Retrocommissioning | The supply air temperature setpoint for the unit ventilators is currently 70°F, while the unoccupied space temperature setpoint is 62°F. This may result in excessive fan run times during unoccupied periods due to the small temperature difference between t
1275 |  | Replace Dishwasher Electric Booster Heater with Propane Heater | Energy Savings | 807 | 660 | [5 empty] | Retrocommissioning | The dishwasher in the kitchen has a 3 kW electric resistance booster heater to elevate the temperature of the hot water. Replacing this with a propane heater could result in a peak demand reduction, as well as cost savings from switching to a cheaper fuel
1275 |  | Investigate Options for Demand Limitng | Energy Savings | 2496 | [6 empty] | Retrocommissioning | The school is on an electric tariff with relatively high demand charges that also includes a ratchet, meaning that the peak demand set during any particular month will determine the billed demand for the next eleven months. We recommend raising awareness
1275 |  | Install Variable Speed Drive to Control Hot Water Pumos | Energy Savings | 1184 | 13460 | [5 empty] | Retrocommissioning | The existing hot water pumps operate at a constant speed regardless of the actual heating demand in the building. By slowing down the pumps to match the flow to the demand using a variable frequency drive, significant energy savings can be achieved. Effic
1275 |  | Continue Upgrading Unit Ventilators | Energy Savings | [7 empty] | Retrocommissioning | Many of the unit ventilators are original equipment from when the building was initially constructed in 1967. These are being replaced gradually as capital funds become available. Ensure that the most efficient units are selected at the time of replacemen
1275 |  | Continue Lighting Upgrades | Energy Savings | [7 empty] | Retrocommissioning | Lighting in a few classrooms has already been upgraded to LED. We recommend continuing with LED lighting upgrades as funds become available, and for classrooms in perimeter areas, consider incorporating daylight dimming controls. Efficiency Vermont may as
1275 |  | Calibrate CO2 Sensors to ensure proper ventilation | Energy Savings | [7 empty] | Retrocommissioning | Ventilation in most areas of the building is controlled to maintain a maximum carbon dioxide concentration of 1,500 ppm. Since CO2 sensors are prone to drifting out of calibration, we recommend implementing a program to periodically calibrate the CO2 sens
1275 |  | Adjust Schedules in BAS to Reflect Actual Occupancy Patterns | Energy Savings | 1139 | 4903 | [5 empty] | Retrocommissioning | Building occupancy schedule in BAS is weekdays from 4 a.m. – 3 p.m. The earliest teachers get to the building is around 6:00 a.m. and students arrive at 7:20 a.m. There is an occupancy schedule set for Wednesdays 3 -8 p.m. due to gym being used during thi
1275 |  | Return Hot Water Pump P-1 to Automatic Control | Energy Savings | 130 | 903 | [5 empty] | Retrocommissioning | Pump P-1 in boiler room was running with no control available through BAS, presumably due to a bad relay. Recommend repairing or replace relay for hot water pump P-1 in boiler room and ensure automatic control through BAS is achieved.
1275 |  | Ensure Adequate Ventilation is being Provided | Energy Savings | [7 empty] | Retrocommissioning | Inadequate ventilation in server room.
1275 |  | Relocate Outside Aire Sensor, other rcx Maintenance Recommendations | Energy Savings | [7 empty] | Retrocommissioning | The outside air temperature sensor used in building automation control sequences is located on the northeast corner of the building. During morning hours, it is in the sun and reading higher than the actual temperature. This can affect operation of equipm
1289 |  | AHU-5 Simultaneous Heating and Cooling | Energy Savings | 18440 | 32344 | [5 empty] | Retrocommissioning | AHU-5 was initially observed to be in cooling mode, while the steam preheat coil 1/3 valve was also open and preheating the supply air. It was determined that the steam valve was leaking by, even when commanded to 100% closed. Savings can be attributed to
1290 |  | AHU Outside Air Balance | Energy Savings | 1028 | 344 | [5 empty] | Efficiency Consulting | All of the hospital’s AHUs currently rely on outside air damper positions as a means of controlling outdoor air flow. Damper position is never reflective of the actual outside air CFM, and when used in this manner typically results in over ventilating and
1291 |  | Terminal Reheats | Energy Savings | [7 empty] | Retrocommissioning | During the qualification phase BAS review, it was believed that some terminal reheat coils associated with AHU-3 and AHU-6 were heating supply air when not enabled by the BAS. After testing it was determined that this was not an issue. A sample of reheats
1292 |  | Unthrottle Balancing Valves on Pump Discharge | Energy Savings | 2981 | 24845 | [5 empty] | Retrocommissioning | • Condenser water pump P-5 has throttled triple duty valve
1292 |  | Operate Cooling Tower Cells in Parallel | Energy Savings | 2400 | 20000 | [5 empty] | Retrocommissioning | • Currently each cooling tower cell is dedicated to a chiller, so that if only one chiller is operating, only one cell and cooling tower fan are operating. It is more efficient to operate both cells in parallel due to the increased surface area for heat r
1292 |  | Optimize Chilled Water Plant Control Sequences | Energy Savings | 9000 | 75000 | [5 empty] | Retrocommissioning | Pump P-5 serving condenser water loop for CH-1 was observed to be operating in HAND, while CH-1 was not operating at the time Recommend Optimize control sequences for chilled water plant operation, including: Chilled water supply temperature control, Sec
1292 |  | Release BAS Overrides and Return Equipment to AUTO Control | Energy Savings | 2691 | 22426 | [5 empty] | Retrocommissioning | Pumps P-1, P-3, and P-4 speeds were overridden to 100% through the BAS (although P-1 and P-3 were off at the time)
1292 |  | AHU Unoccupied Programming | Energy Savings | 18933 | 82655 | [5 empty] | Retrocommissioning | AHU-1 and AHU-2 do not currently have any airflow setback schedules, and the spaces served by them have no temperature setback schedules. A setback for these air handlers and associated spaces can be accomplished by programming an occupied / unoccupied sc
1293 |  | ASHRAE 36 Control Damper Operations | Energy Savings | 3616 | 27049 | [5 empty] | Retrocommissioning | It was observed during the development investigation that several of the air handlers had fan speeds that were higher during minimum outside air mode than when in an economizer mode. This indicates that there was likely a restriction on the fan system dur
1294 |  | Face/Bypass Damper Operation | Energy Savings | [7 empty] | Retrocommissioning | It was observed that no energy savings will be associated with this measure. This measure is currently being implemented with the first phase of RCx measures as it was part of the new economizer control and temperature control sequences being implemented
1297 |  | Unnecessary or redundant MERV air filters in AHUs | Energy Savings; First Cost; O&M | 18990 | 123000 | [5 empty] | MEP Cx | › Unnecessary or redundant MERV air filters within AHUs can significantly reduce energy efficiency and increase O&M burden with no additional benefits to air quality. Cx Associates identified unnecessary intermediate MERV air filters in the design of ever
1297 |  | Change three-way valves in CRAC units to two-way | Energy Savings | 13945 | 107266 | [5 empty] | MEP Cx | We suggested changing three-way valves in CRAC units to two-way
1297 |  | Reduce design water pressure drop through chiller | Energy Savings |  | 25000 | [5 empty] | MEP Cx | During design review for the new Central Utility Plant (CUP) chiller, Cx Associates identified an opportunity to improve energy efficiency by reducing the design water pressure drop through the condenser and evaporator of the new 2000 Ton chiller. The ch
1298 |  | Return Pump Operation to AUTO and Release BAS Oerrides | Energy Savings | 283 | 2106 | [5 empty] | Efficiency Consulting | While reviewing BAS functionality, we found that the pump serving Zone 8 (P-37) was showing a status of ON even though it was commanded OFF, indicating the pump is operating in HAND. Additionally, the zone valve position for Zone 6 was found to be overrid
1299 |  | Replace Damaged Snowmelt Sensor | Energy Savings | 7762 | 3043 | [5 empty] | Problem Solving | Functional testing was performed to confirm proper snowmelt sensor operation by spraying sensors with water and observing whether sensor status changed from “Dry” to “Wet” in the BAS. All sensors were found to be functioning properly except for the sensor
1300 |  | Reduce Snowmelt Mode Slab Temperature Setpoints | Energy Savings | 3043 | [6 empty] | Problem Solving | During review of BAS settings, we discovered that two of the zones (Zone 8 and Zone 9) had elevated snowmelt mode slab temperature setpoints of 70°F and 60°F respectively. Again, this is likely related to the issue regarding improper sensor location for Z
1301 |  | Replace Missing Roof Mainfold Cabinet Door and Bleached Piping | Energy Savings | 0 | [6 empty] | Eval / Measurement and Verification (EM&V) | The cabinet containing one of the roof zone supply manifolds is missing its door, resulting in exposure to sunlight and bleached piping. PEX tubing typically has a sunlight exposure rating of 20 hours, so the integrity of these pipes is most likely compro
1302 |  | Reduce Excessive Outside Air Flow | Energy Savings | 5223 | 1820 | [5 empty] | Retrocommissioning | Currently, the AHUs serving the campus center are programmed to introduce a minimum outside airflow whenever the spaces are occupied and will increase outside air if necessary to maintain CO2 levels below 900 ppm. However, most of the units appear to be i
1302 |  | Optimize Gym AHU Operation | Energy Savings | 2088 | 16682 | [5 empty] | Retrocommissioning | The following issues were observed for the air handling unit serving the gymnasium: The supply and return fans on the gym air handling unit are equipped with variable frequency drives (VFDs), but are currently operated manually as constant speed fans; The
1302 |  | Optimize Pool AHU Operation | Energy Savings | 3082 | 30381 | [5 empty] | Retrocommissioning | The pool air handling unit supplies conditioned air to the natatorium to maintain temperature and relative humidity setpoints. Humidity can be controlled to the extent possible by varying the amount of outside air introduced, but there is no mechanical de
1302 |  | Reduce Pool Pump Water Flow | Energy Savings | 880 | 7031 | [5 empty] | Retrocommissioning | The 15-horsepower pool filter pump operates at 48 Hz (80% speed, 7.7 kW) continuously 24/7. The fixed speed was presumably set at the time of VFD installation in order to meet minimum required water exchange rates, and saves significant energy compared t
1302 |  | Install Swimming Pool Cover | Energy Savings | 5352 | [6 empty] | Retrocommissioning | Currently, the pool stays uncovered when not in use, resulting in significant evaporation and associated heat loss, along with increased humidity in the natatorium. Recommend installing a pool cover and establishing a daily procedure for covering and unco
1302 |  | Budget for Replacement of Corroded Snowmelt Sensors | Energy Savings | 0 | [6 empty] | Retrocommissioning | We observed that several snowmelt sensors are suffering from corrosion. While the sensors were operating properly at the time of our site visit, they may cease functioning at any time and should be replaced soon.
1304 |  | Permorm Rebalancing of System | Energy Savings | 0 | [6 empty] | Commissioning | Facilities staff indicated that the snowmelt system suffers from balancing and flow issues. System balancing will ensure that all zones receive the required flow.
1305 |  | Optimize Control Sequence for Pump P-21 | Energy Savings | 1176 | 8736 | [5 empty] | Retrocommissioning | The pump serving the snowmelt loop header is equipped with a VFD and designed to modulate speed to maintain a return water temperature of 125°F. However, a trend data review showed that the pump speed does not appear to be modulating appropriately. This w
1306 |  | Clean Air Handling Equipment Filters | Energy Savings | 200 | 1700 | [5 empty] | Retrocommissioning | Kitchen MAU are extremly dirty filters but BAS was indicating they are clean, sugginting that the BAS filter pressure switch is broken or out of callibration. Recommend perforing preventative maintenance check, including changing the filters on the MAU an
1306 |  | Rebalance ERV and MAU | Energy Savings | 400 | 3300 | [5 empty] | Retrocommissioning | The MAU was activly bypassing the heat exchanger core, however, the graphic showed it not in bypass. The locker room ventilation appears to be poor due to the ERV running at a very low speed. The odor in the rooms was very prominent and there is condensat
1306 |  | 3rd Floor Thermostat Repair | Energy Savings | 1000 | -2500 | [5 empty] | Retrocommissioning | Rooms on the third floor were designed to have one thermostat control (2x) heat pumps. This results in the thermostats being parallel wired to both heat pumps. This caused fuses to blow in the heat pumps because two independent 24 val control sources were
1306 |  | 4th & 5th Floor Thermostat Replacement | Energy Savings | 900 | 1700 | [5 empty] | Retrocommissioning | Poor thermostat placement causing the two heat pumps to be able to simultaneously heat and cool the same space. It is recommeded that the existing thermostats serving the guest bedrooms should be removed and those heat pumps should be interlocked in the
1306 |  | Tower Sensor Well Repair | Energy Savings | 400 | 2600 | [5 empty] | Retrocommissioning | The tower was completely plugged up and had not been cleaned in over a year. The result of that was a poor heat rejection delta (2.5F). Also found the setpiont were not coordinated with the heat pumps factory requirements. Recommend installing a new well
1306 |  | Correct the Series Pumping | Energy Savings | 300 | 2500 | [5 empty] | Retrocommissioning | The high temp heating loop is served by a pair of 3 horsepower pumps. They pump into a modulating three way mixing valve which diverts injects heat into hybrid heat pump loops. During cold weather events, this configuration can result in series pumping ,
1306 |  | Repair Broken Sensors | Energy Savings | [7 empty] | Retrocommissioning | The controlling temperature sensor for the cooling tower is improperly installed. It appears that during construction the sensor thermowell was installed in the cooling towere supply pipe but should have been instaled in the return pipe. The sensor was re
1306 |  | COMPLETED- Cooling Tower Maintenance | Energy Savings | 4300 | 31700 | [5 empty] | Retrocommissioning
1306 |  | Condenser Water Loop Optimization | Energy Savings | 11100 | 22700 | [5 empty] | Retrocommissioning | This measure would involve developing upgraded control sequences that would provide better temperature control of the Bulldog heat pump condenser loop during shoulder seasons. We suspect that there is a significant opportunity to optimize the loop control
1306 |  | Thermostat Networking | Energy Savings | 11500 | 42100 | [5 empty] | Retrocommissioning | This measure develops a guest room thermostat upgrade that would allow the Bulldog heat pumps to be networked. This measure can be developed independently from D-1, however, there will be an increased benefit to developing both measures together. Cx asso
1306 |  | Add Occupancy Schedule to BAS for ERV-1 | Energy Savings | 649 | 3641 | [5 empty] | Retrocommissioning | No apparent schedule implemented in the BAS to control equipent. Even though ERV-1 supply and exhaust fans are equpped with VFD's they run constantly at 100% speed.
1306 |  | Add Occupancy Schedule to BAS for MAU-1 | Energy Savings | 1629 | 6965 | [5 empty] | Retrocommissioning | No apparent schedule implemented in the BAS to control equipent. MAU-1 supply fan is overridden to 75% for all hours.
1306 |  | Optimize Fan Coil Unit Control | Energy Savings | 1026 | 7626 | [5 empty] | Retrocommissioning | Adjust fan coil unit controls so that FCU fans shut off during the cooling season rather than running in an attempt to meet cooling setpoints. If cooling will not be added at any point in the future, consider removing DX cooling coils from fan coil units,
1306 |  | Interlock Room Occupancy Schedules with Booking System | Energy Savings | 1763 | [6 empty] | Retrocommissioning | Interlock Room Occupancy Schedules with Booking System
1306 |  | Optimize Exterior Lighting Control | Energy Savings | 338 | 2513 | [5 empty] | Retrocommissioning | Investigate the capabilities of a Winona path lighting controller and potential to optimize exterior lighting control.
1306 |  | Optimize Hot Water supply Temperature Reset Control | Energy Savings | 882 | [6 empty] | Retrocommissioning | The differential pressure in the hot water loop is a fixed value of 13psi. There may be an opportunity to decrease this or permorm a reset based on the number of open valves in the loop. Investigate the potential for optimizing hot water supply temperatur
1306 |  | Investigate Large Summer Time Load | Energy Savings | 337 | 2504 | [5 empty] | Retrocommissioning | The monthly electric energy consumption baseload is aroudnd 10,000kWh with a significant increase during the summer months due to cooling energy use and golf cart battery charging.
1306 |  | Insure Proper Exhaust for Batter Charging Area | Energy Savings | 165 | -1229 | [5 empty] | Retrocommissioning | Ensure exhaust fan (EF-1) and supply fan (SF-1) serving the golf cart storage area operate whenever batteries are charging in order to provide adequate ventilation air.
1306 |  | Install CCHP to Supplement Electric Resistance Heat | Energy Savings | 4850 | 40149 | [5 empty] | Retrocommissioning | The seven existing electric storage heaters can provide approximately 95,000 Btu/h at maximum capacity when the fans are operating to draw heat from the storage core. Through discussion with the manufacturer (Steffes) it was determined that the heaters ou
1306 |  | Interlock Operation of Adjacent Zones | Energy Savings | 0 | [6 empty] | Retrocommissioning | We found that a couple of the snowmelt zones had their controlling sensors located in an adjacent zone, which caused problems with snowmelt control. One potential solution to ensure that the system operates effectively is to add programming to interlock t
1309 |  | Reduce VAV Box Minimum Flow Rate | Energy Savings | 2461 | 12120 | [5 empty] | Retrocommissioning | VAV box minimum flow rates were set as high as 80% of the maximum box flow. Unclear why it was set so high. We reccommended reducing minimum flow rates which would result in fan energy savings as well as heating and cooling savings.
1309 |  | Static Pressure Reset | Energy Savings | 1188 | 7570 | [5 empty] | Retrocommissioning | Rooftop unit supply fans currently operate to maintain a fixed static pressure of 1.4-1.5 in w.g. at all times. While this static pressure may be necessary during times of peak cooling demand, the s
1309 |  | Improve Economizer Operations | Energy Savings | 714 | 4550 | [5 empty] | Retrocommissioning | Analysis of 15-minute electric interval data suggested that mechanical cooling is operating at outside air temperatures as low as 50°F. The energy recovery wheel bypass dampers in the rooftop units may not be operating properly, resulting in undesirable e
1309 |  | Optimize Dehumidification Control Sequence | Energy Savings | 239 | 1520 | [5 empty] | Retrocommissioning | The facility manager mentioned humidity is not controlled well in some areas, which can be a serious problem for finished food products. We believe facility operation would benefit from a thorough commissioning of the AAON rooftop units, including functio
1309 |  | Confirm Calibration of Temperature and Humidity Sensors | Energy Savings | 366 | 1620 | [5 empty] | Retrocommissioning | Temperature and relative humidity sensors can drift out of calibration over time, resulting in increased energy use, poor control of interior conditions, or both. Relative humidity sensors are especially prone to drift. Data loggers were deployed to a few
1309 |  | Integrate CaptiveAire Controls with BAS | Energy Savings | 913 | 4040 | [5 empty] | Retrocommissioning | Currently, the CaptiveAire kitchen exhaust hoods are manually and are not visible or controlled through the BAS. When the building was these were operating in an uncontrolled fashion for several months, resulting in energy consumption. We recommend adding
1319 |  | Cooling Tower Improvements | Energy Savings | 3100 | 9600 | [5 empty] | Retrocommissioning | The cooling tower has basic controls, including a fixed speed 10 HP sump motor and a basin heater. The cooling tower was reported to be rejecting heat in January and February of 2016. Replacing these factory controls with programmable BAS controllers may
1319 |  | Heat Rejection into Pools | Energy Savings | 10200 | 16500 | [5 empty] | Retrocommissioning | Given the mechanical proximity of the condenser water loop and the pool heating loop, there may be an energy savings opportunity around waste heat. The pool and hot tub have a 3,000MBH boiler dedicated to heating them and the cooling tower rejects up to
1319 |  | Pool System Optimiztion | Energy Savings | 2000 | [6 empty] | Retrocommissioning | There is little integration with the BAS and the pool system. The pool is suspected to be contributing to the high EUI of the building (from propane consumption). This measure is to disaggregate its impact on Burke’s propane consumption. Given the prev
1319 |  | Snow Melt System Optimization | Energy Savings | 4200 | 13500 | [5 empty] | Retrocommissioning | Due to the reported behavior of the snow melt system, the system should be fully tested and metered. Snow melt is also suspected of being one of the contributing factors to the building’s high EUI. This measure would develop systematic testing of the sn
1319 |  | ERV Occupancy Interlock | Energy Savings | 2000 | 14000 | [5 empty] | Retrocommissioning | It was reported that the Telkonet thermostats are integrated into the BAS. Using the occupancy data associated with this system, it may be possible to interlock ERVs with the heat pumps downstream in such a way that they would only run if a guest was occ
1339 |  | Implement Unoccupied Temperature Setback | Energy Savings | 146 | 532 |  |  | 57 |  |  | Retrocommissioning | While examining settings on the single operating Nest thermostat, we found that the heating and cooling temperature setpoints were not being set back during unoccupied hours. This measure was implemented during our site visit and should result in modest h
1339 |  | Clean Condensing Unit Fins | Energy Savings | 33 | 213 | [5 empty] | Retrocommissioning | Condensing unit coil fins are fouled, hampering heat rejection and reducing efficiency.Clearing the fins of dirt and debris will increase heat transfer effectiveness and reduce cooling energy.
1339 |  | Undergo Comprehensive Envelope and HVAC Renovation | Energy Savings | [7 empty] | Retrocommissioning | Capital investment is required in order to meaningfully improve the building’s comfort problems. The building owner recognizes this and has already begun pursuing various projects, including: Replacing existing windows on the south façade with high perfor
1341 |  | Recommission Sensor and Varify Proper Balance | Energy Savings | 380 | 4420 | [5 empty] | Retrocommissioning | There are a number of chronic comfort issues reported by building occupants. In one office, airflow was at a relatively high velocity and blowing on occupants. Further, the thermostat was located close to an open doorway next to an adjacent zone, resultin
1341 |  | Interlock Heating in Contemplative Space with Occupancy | Energy Savings | 119 | 1380 | [5 empty] | Retrocommissioning | The heat was on in the “Lens” building contemplative space, which is an out-building directly adjacent to CAPA’s main structure. The space is equipped with a mechanical remote skylight/shutter which was found open, despite the space being served by hot wa
1341 |  | Enable Hot Gas Reheat for Humidity Control | Energy Savings | [7 empty] | Retrocommissioning | The geothermal terminal heat pumps are equipped with DX reheat coils, which can be utilized for dehumidification. The controls required for this option to function were not installed at the time of construction, however humidity control in the space is of
1356 |  | Implement Occupancy Schedules for RTUs and ERU | Energy Savings | 13950 | 104025 |  |  | 5375 |  | 0 | Retrocommissioning
1356 |  | Raise Chilled Water Supply Temperature Setpoin | Energy Savings | 240 | 1525 |  |  | 0 |  | 6 | Retrocommissioning
1356 |  | Optimize Static Pressure Reset Control | Energy Savings | 221 | 2435 |  |  | 0 |  | 0 | Retrocommissioning
1356 |  | Variable Speed Hot Water Pumps | Energy Savings | 1933 | 21090 |  |  | 0 |  | 0.2 | Retrocommissioning
1359 |  | Optimize Control of Snowmelt System | Energy Savings | 6389 | [6 empty] | Retrocommissioning | With outdoor air temperatures in the mid 80’s, when we enabled the snowmelt controls, hot water began to run out to the slab. The slab was well above a winter slab idle temperature. While there is a slab mounted temperature/moisture sensor, it appears tha
1359 |  | Turn off Distribution Pump in Summer | Energy Savings | 941 | 2014 | [5 empty] | Retrocommissioning | A circulation pump in City Hall was found to be operating, meaning it was circulating hot water throughout the Fire Station during the summer months. This will lead to wasted heating energy during the summer operating period and unnecessary summer heating
1359 |  | Insulate Basement HW Piping | Energy Savings | 470 | [6 empty] | Retrocommissioning | The hot water loop running through the basement of the station is 1-1/2” steel and is substantially uninsulated. The ¾” copper snowmelt loop piping running within the basement is also uninsulated. Significant heat loss can occur due to this uninsulated pi
1359 |  | Summer District Pump DP Control | Energy Savings | 777 | 5288 |  |  |  |  | 1.47 | Retrocommissioning | While on site, we noticed the distribution pump for summer hot water was operating at 100% speed (60 hz). The differential pressure (DP) setpoint was satisfied, however the pump was generating much more pressure than required to meet setpoint. The DP read
1359 |  | Piping Insulation at Service Enterancfe | Energy Savings | 2935 | [6 empty] | Retrocommissioning | During our walkthrough, we found a few places where insulation was missing on piping at the building service entrance; at these locations, heat loss would end up on the City’s side of the BTU meter. Overall the delivery efficiency of the district loop dur
1359 |  | High-Efficiency Boiler Retrofit, with Summer SWT Reset | Energy Savings | 6849 | [6 empty] | Retrocommissioning | For the long term, we recommend considering a higher efficiency generating source for summer heating, which would be most economically viable during an upgrade. At present, the boiler plant is operating in the 80% efficiency range, which is reasonable for
1359 |  | Replace Metal Halide Fixtures | Energy Savings | 142 | 1139 | [5 empty] | Retrocommissioning | There are a number of metal halide fixtures on the exterior of the building, in the hallway between the offices/lab and the Process Room, and over the process room floor. According to operators, the process room lighting is not utilized except during cert
1359 |  | Enable OA Based Boiler Disable | Energy Savings | 791 | 504 | [5 empty] | Retrocommissioning | The heating plant consists of an oil-fired boiler, which generates 180F hot water year-round. Hot water needs in the space are almost exclusively limited to heating season. At a minimum, hot water supply water temperature could be reduced.
1359 |  | Replace DX Dehumidification Units | Energy Savings | 4375 | 3500 | [5 empty] | Retrocommissioning | The dehumidification units in the Process Room and Bulk Chemical room are older, and high efficiency equipment is now available. While replacement prior to failure is not cost effective on an energy savings basis alone, when units begin to fail, we recomm
1363 |  | Chiller Plant dP Setpoint | Energy Savings |  | 16072 |  |  |  |  | 2.99 | Retrocommissioning | Relocate chilled water supply dP sensor 2/3 of the distance down the longest or heaviest used pipe run and establish the new dP setpoint with Cx Associates.Notes: The existing dP sensor (labeled actual on BAS) was left in the same position. A new dP senso
1363 |  | Boiler dP Setpoint | Energy Savings |  | 9120 |  |  |  |  | 1.69 | Retrocommissioning | Install a power meter for monitoring the chiller.There is a next step to this work, which is the development of a kW/ton cooling algorithm that is described in the Open Items section of this memo.
1363 |  | HRU dP Setpoint | Energy Savings |  | 22490 |  |  |  |  | 3.42 | Retrocommissioning | Relocate the hot water pump dP sensor 2/3 out in the hot water system. This new location will enable the sensor to respond more accurately to the small changes in the system’s demand. Notes: The existing dP sensor (labeled actual on BAS) was left in the s
1363 |  | Garage Exhaust Fan Speed | Energy Savings |  | 969 |  |  |  |  | 8.21 | Retrocommissioning | Provide VFD, start-up and programming for the existing exhaust fan. Notes: The VFD was already programmed to operate at a maximum 50% speed upon a CO call. We checked the historical 10-day trend data and see that the garage has not gone above 42 ppm for m
1366 |  | Office Areas Rcommissioning- Verify Zone/Control Mapping | Energy Savings | 472 | [6 empty] | Retrocommissioning | Recommend recommissioning office areas to ensure zones are correctly configured and that sequences/setpoints result in discrete zone control to whatever extent possible. This may mean that the perimeter radiation, if configured as only one zone, has one s
1366 |  | Service Areas Recommissioning- Review Setpoints and Controls | Energy Savings | 707 | [6 empty] | Retrocommissioning | Setpoints should be unified. These spaces are not on the BAS, and as such, we recommend either BAS integration or a smart(er) thermostat. A smart thermostat could result in better control (and ideally remote monitoring) of bus parking, service, and shop s
1366 |  | Decouple DHW System to Achieve Condensing Boier Efficiency | Energy Savings | 1650 | [6 empty] | Retrocommissioning | Due to the constant operating temperature of 150F-180F, which may have been driven by a domestic hot water heating priority configuration, the boilers are not condensing and are likely operating in the high 80% range. If domestic hot water can be generate
1366 |  | Interior Lighting LED Retrofits | Energy Savings | 6169 | 42644 | [5 empty] | Retrocommissioning | The interior bus maintenance and parking areas have high bay linear fluorescent 4-lamp T5 fixtures. T5 fixtures are obsolete and more difficult to maintain due to a shorter lifespan compared to an LED. LEDs are also significantly more efficient. To replac
1373 |  | Reduce Cooling Towere Pump Minimum Speed | Energy Savings | [7 empty] | Retrocommissioning | When the throttling valve has been opened 100%, the pressure the pump must overcome will be greatly reduced. This means the pump will not require as much speed to push the water through the piping and its minimum speed can be reduced. We recommend progr
1373 |  | Relocate/ Calibrate BAS Outside Aire Temperaature Sensor | Energy Savings | 50 | 250 | [5 empty] | Retrocommissioning | This sensor, which determines the operation of the economizer, is located such that it sees direct sunlight during the middle of the day. During shoulder seasons, this will falsely turn off the economizer and operate Union Station using the chiller. We r
1373 |  | Install VFD on the Supply and Return Fans of MAU#2 | Energy Savings | 3850 | 24700 | [5 empty] | Retrocommissioning | The make-up air unit for the Cornerstone building has (2) constant speed fans and operates independently of the CO2 levels in the building. The unit could be placed on the BAS and have VFDs installed on the supply and exhaust fans so that the fans could
1373 |  | Replace Garage Ligh Bulbs with LED Bulbs | Energy Savings | 830 | 4900 | [5 empty] | Retrocommissioning | The existing garage fixtures are 80-watt induction type fixtures that were installed in 2012 and are on 24/7. Upon bulb failure, we recommend replacing them with LED bulbs. A 65-watt LED can provide the same lumens as the current fixture while producing
1376 |  | Boiler HW Suppl Temperature Reset | Energy Savings | 2250 | [6 empty] | Retrocommissioning | It appears the boilers operate at a constant 160F supply water temperature, which prevents the boilers from condensing flue gas and results in lower operating efficiency (likely the mid 80% range). By implementing a hot water supply (HWS) temperature rese
1376 |  | HVAC/Lighting Recommissioning | Energy Savings | 8723 | 52116 |  |  |  |  | 12 | Retrocommissioning | Believe they could significantly from a recommissioning effort, in which key systems are recommissioned to meet intended design/required operating points with the objective of saving energy, improving comfort, and decreasing operating headaches. HVAC and
1376 |  | Refrigeration- Variable Speed CDW Pumping (3 pumps) | Energy Savings | 3020 | 30090 |  |  |  |  | 4.3 | Retrocommissioning | The existing refrigeration condenser water pumps (three nominal 1 ½ to 2 horsepower), moving a 40% PG antifreeze solution, are traditional in-line constant speed pumps. These pumps have very high annual run hours and consume, in total, about 40,000 kWh pe
1376 |  | Refrigeration - Variable Speed Condenser Fan Motor | Energy Savings | 3447 | 38000 | [5 empty] | Retrocommissioning | The refrigeration dry cooler condensers use multiple constant speed fans, staged sequentially as required to maintain a saturated condenser temperature (SCT) setpoint. This type of condenser fan control is the industry standard, and universally common. On
1376 |  | Refrigeration- Heat Recovery/ Head Pressure Control Recommissioning | Energy Savings | 5736 | 63225 | [5 empty] | Retrocommissioning | The refrigeration rack head condensing pressure/temperatures appear to be currently held higher than required year-round to facilitate heat recovery, using a fixed, constant saturated condensing temperature (SCT) setpoints. While recovering beneficial hea
1378 |  | Energy Wheel Bypass Damper Operation | Energy Savings | [7 empty] | Commissioning | During FPT Cx found that the ERV wheel was being bypassed during normal operation since the controls system was attempting to only allow 6000 CFM through the wheel, which is all it was rated for. The controls system was looking at the supply air CFM inst
1378 |  | Static pressure reset | Energy Savings | [7 empty] | Commissioning | Static pressure reset was implemented on AHU. It was found that most VAV boxes were typically operating at minimum damper position, so this helped to improve operation as well as save energy.
1387 |  | LED Lighting Upgrade | Energy Savings | 15756.7418 | 101082 | 0 |  |  | 0 | 28.7 | Analysis/Audit | The existing lighting consists primarily of recessed 3-lamp linear fluorescent troffers with “Super” T8 (28-watt) lamps and high efficiency electronic ballasts. While compact fluorescent and incandescent lamps have been replaced with LEDs in a couple of a
1387 |  | Minimize 24/7 Building Operation | Energy Savings | 10276.8975 | 68488 | 352.7 |  |  | 0 | 0 | Analysis/Audit | Based on a review of the electric meter interval data and discussion with facilities staff, we discovered that the building was placed in occupied mode 24/7 from mid-January through April, as well as during July and August. This operation was used order t
1387 |  | Optimize BAS Occupancy Schedules | Energy Savings | 9817.008 | 62400 | 364.8 |  |  | 0 | 0 | Analysis/Audit | While mechanical equipment operates according to schedules during normal building operation, there may be an opportunity for optimizing the occupied schedules to more accurately reflect actual building operating patterns. For example, some of the equipmen
1387 |  | Install VFDs for Hot Water Pumps | Energy Savings | 1304.5369 | 13548 |  |  |  | 0 | 0 | Analysis/Audit | The existing hot water loop pumps serving the Annex operate at a constant speed regardless of the actual demand at the heating coils being served. By installing variable frequency drives (VFDs) to control the pumps, pump speed could modulate based on flow
1387 |  | Maximize Boiler Efficiency | Energy Savings | 732.6 | 0 | 0 |  |  | 222 | 0 | Analysis/Audit | During the summer months when the district steam system is not operating, two propane-fired boilers provide hot water to reheat coils in the Annex. The hot water supply temperature setpoint appears to be 130°F based on an examination of trend data, with t
1387 |  | Optimize Liebert System | Energy Savings | 1545.0798 | 12842 |  |  |  | 0 | 1.47 | Analysis/Audit | There were originally several Liebert units in the building to provide cooling for data closets, but most of them have been removed over the years, as equipment in the data closets has moved elsewhere. There is now only one unit remaining in Computer Room
1387 |  | Variable Flow Chilled Water Pumping | Energy Savings | 1445.9869 | 15017 | 0 |  |  |  | 0 | Analysis/Audit | The pumping configuration for the centrifugal chiller (CH-1) consists of a primary-only constant speed 15-hp chilled water pump and constant speed 15-hp condenser water pump. We recommend installing a variable frequency drive (VFD) to modulate the chilled
1387 |  | LED Lighting Upgrade | Energy Savings | 7904.4449 | 55934 | 0 |  |  |  | 12 | Analysis/Audit | The existing lighting consists of a mixture of compact fluorescent lamps (CFL), linear fluorescent fixtures and light emitting diode (LED) lamps. While BGS has been replacing CFLs with LEDs piecemeal as they fail, we recommend pursuing a comprehensive LED
1387 |  | Integrate Rooftop Snowmelt into BAS | Energy Savings | 639.9305 | 5774 | 0 |  |  |  | 2.4 | Analysis/Audit | The rooftop snow melt electric resistance heating cable is currently controlled through a manual switch and operates continuously throughout the winter. Often these are left on well into the spring months, since operators forget to turn them off at the en
1387 |  | Install Air Curtain at Building Entrance | Energy Savings | 984.8307 | 1954 | 16 |  |  |  | 18 | Analysis/Audit | Currently the main entrance doors to the building are left open during the summer months to provide a welcoming environment for public tours. This results in a large amount of uncontrolled outside air infiltration and corresponding increased heating and c
1387 |  | Install VFDs for Hot Water Pumps | Energy Savings | 1384.265 | 14376 | 0 |  |  |  | 0 | Analysis/Audit | The existing hot water loop pumps operate at a constant speed regardless of the actual demand at the heating coils being served. By installing variable frequency drives to control the pumps, pump speed could modulate based on flow requirements, resulting
1387 |  | ECM Motors for Walk-In Evaporator Fans | Energy Savings | 290.4835 | 2955 | 0 |  |  |  | 0.34 | Analysis/Audit | The evaporator fans serving the walk-in cooler and freezer in the kitchen run continuously 24/7. These fans not only consume electricity to operate, they also create heat that must be removed by the refrigeration system. We recommend replacing the existin
1387 |  | Optimize AHU Operation | Energy Savings | 1194.9589 | 12410 | 0 |  |  |  | 0 | Analysis/Audit | While the age and configuration of the air handling units coupled with the need to maintain appropriate environmental conditions for the many historical paintings in the building places a limit on what can realistically be achieved, there may still be opp
1387 |  | Demand Control Kitchen Ventilation | Energy Savings | 783.7669 | 2686 | 50.3 |  |  |  | 0 | Analysis/Audit | Currently the kitchen exhaust hood fan and associated makeup air unit supply fan run at a constant speed whenever the hood is turned on and operating. Demand control kitchen ventilation (DCKV) involves adding VFDs to the fans to modulate fan speed to refl
1387 |  | LED Lighting Upgrade | Energy Savings | 2528.574 | 15405 | 0 |  |  |  | 6.3 | Analysis/Audit | The existing lighting consists primarily of linear fluorescent fixtures with “Super” T8 (28-watt) lamps and high efficiency electronic ballasts. The main fixture types include 3-lamp 2’x4’ recessed troffers and 2-lamp 4’ suspended linear pendants. While t
1387 |  | Optimize BAS Occupancy Schedules | Energy Savings | 1413.302 | 6934 | 77 |  |  |  | 0 | Analysis/Audit | While the air handling units operate according to schedules implemented in the BAS, there may be an opportunity for optimizing these occupancy schedules to more accurately reflect actual building operating patterns. For example, many of the AHUs are sched
1387 |  | Replace R-22 Condensing Units | Energy Savings; Code / Safety; O&M | 1093.48 | 6502 | 0 |  |  |  | 8.4 | Analysis/Audit | Several of the older condensing units serving the split systems are at the end of their useful life and use R-22 refrigerant, which can no longer be produced or imported into the United States as of January 1, 2020. Therefore, these units should be replac
1387 |  | Makeup Air Unit Heat Recovery | Energy Savings | 1189.02 | 0 | 114 |  |  |  | 0 | Analysis/Audit | The makeup air unit (MAU) provides 100% outside ventilation air to the third and fourth floors. We recommend replacing this unit with an energy recovery ventilator (ERV) to recover heat from exhaust air that can be transferred to the supply air via a plat
1387 |  | Replace Aging Refrigerators | Energy Savings | 155.86 | 1348 | 0 |  |  |  | 0.2 | Analysis/Audit | There are several refrigerators in kitchen areas and break rooms throughout the facility. Electricity consumption for refrigerators is driven primarily by the size and age of the unit. Older refrigerators can use much more energy than more modern energy e
1387 |  | Plug Load Management | Energy Savings | 399.5251 | 4540.0577 | [5 empty] | Analysis/Audit | Plug loads are estimated to comprise over 25% of the electricity consumption at the building. There are a number of options for effectively managing plug loads , including the following: 1. Behavioral changes – Encourage building occupants to power dow
1387 |  | Single Zone VAV Systems | Energy Savings | 822.536 | 9347 | 0 |  |  |  | 0 | Analysis/Audit | The air handling units serving the facility are currently constant volume systems with constant speed supply fans. This measure would convert the units to single zone variable air volume systems by installing variable frequency drives (VFDs) on the supply
1387 |  | Replace Standard Efficiency Motors with Premium Efficiency | Energy Savings | 72.738 | 615 |  |  |  |  | 0.1 | Analysis/Audit | Premium efficiency motors are more efficient than motors that are minimally compliant with federal standards. Due to the relatively small motor sizes and low operating hours, early replacement of the motors is not a cost-effective measure. However, premiu
1387 |  | LED Lighting Upgrade | Energy Savings | 442.398 | 2700 |  | 0 |  |  | 1.1 | Analysis/Audit | The existing lighting consists primarily of linear fluorescent fixtures with T8 lamps and high performance electronic ballasts (“Super T8s”). We recommend pursuing a comprehensive LED lighting upgrade to retrofit the existing fixtures. Along with the bene
1387 |  | Unoccupied Temperature Setback | Energy Savings | 190.008 | 0 |  | 190.008 |  |  | 0 | Analysis/Audit | Currently the thermostat in the building maintains the heating space temperature setpoint at 72°F during all hours. Since the building is generally unoccupied overnight from 5 p.m. – 7 a.m. and on weekends, we recommend implementing an unoccupied heating
1387 |  | Cold Climate Heat Pump | Energy Savings | 497.702 | -7884 |  | 1414.91 |  |  | -2.4 | Analysis/Audit | We investigated a ducted cold climate heat pump system that could be used to provide heating down to outdoor air temperatures of 5°F. This can be used in conjunction with the existing oil-fired furnace, which would operate when temperatures are below 5°F
1387 |  | Energy Recovery Ventilator | Energy Savings; IAQ | 216.538 | 111 |  | 113.68 |  |  | 0.5 | Analysis/Audit | Currently the only mechanical ventilation being provided to the building is through the shop exhaust fan, which may only operate intermittently. Given what we know regarding the increased importance of ventilation, especially during COVID-19, we recommend
1387 |  | Refrigerator Replacement | Energy Savings | 35.973 | 303 |  | 0 |  |  | 0.05 | Analysis/Audit | There is a refrigerator in the break room. Electricity consumption for refrigerators is driven primarily by the size and age of the unit. Older refrigerators can use much more energy than more modern energy efficient units. When the existing refrigerator
1387 |  | Door Weather Stripping | Energy Savings | 116.41 | 0 | 7 |  |  |  | 0 | Analysis/Audit | Air leakage was observed around all of the exterior doors in the building. On doors that are still in good shape, the most cost-effective measure is to check the thresholds, sweeps, and weather-stripping once a year and replace as needed. Even old doors c
1387 |  | Basement Insulation | Energy Savings | 563.757 | 0 | 33.9 |  |  |  | 0 | Analysis/Audit | We recommend insulating the basement walls with 3 inches of closed-cell spray foam, starting at the underside of the floor above to at least 2 feet below grade. In order to reach the top of the wall, the plaster ceiling will need to be removed at the peri
1387 |  | Attic Slope + High Roof Renovations | Energy Savings | 1170.752 | 0 | 70.4 |  |  |  | 0 | Analysis/Audit | The attic mansard slopes and high flat roof have metal on the exterior (presumably uninsulated on the exterior of sheathing) but are insulated on the interior side of the sheathing with foil-face fiberglass batts. However, there is no air barrier and curr
1387 |  | Mansard Wall + Low Roof Renovations | Energy Savings | 3788.314 | 0 | 227.8 |  |  |  | 0 | Analysis/Audit | The mansard walls and roof have a metal exterior finish and no insulation on the interior side of the sheathing. We are unsure what the layers are beneath the metal, but it is unlikely, due to its age and profile thickness, that there is any insulation on
1387 |  | Exterior Wall Renovations | Energy Savings | 5038.89 | 0 | 303 |  |  |  | 0 | Analysis/Audit | Mass masonry buildings, like this one, were historically built without the typical air, vapor, water, and thermal control layers that are found in modern day construction. The walls are constructed using only brick and mortar that is layered in multiple r
1387 |  | Window Replacement | Energy Savings | 1405.235 | 0 | 84.5 |  |  |  | 0 | Analysis/Audit | Most of the windows in the building are wood frame, single-hung, single-pane windows with weighted pulleys and an exterior storm. The wood frame windows, after so many years of wear and tear, do not create a tight air seal when closed, and the single pane
1387 |  | LED Lighting Upgrade | Energy Savings | 2046.0124 | 14030 |  |  |  |  | 4.358 | Analysis/Audit | The existing lighting consists primarily of linear fluorescent fixtures with T8 lamps and high performance electronic ballasts (“Super T8s”). The main fixture types include 2’x4’ recessed troffers and suspended linear pendants. While the existing fluoresc
1387 |  | Retrocommissioning | Energy Savings | 556.334 | 2500 | 15 |  |  |  | 1.4 | Analysis/Audit | While reviewing the BAS graphics, we noticed a number of potential opportunities we would classify as retrocommissioning measures, which are low-cost measures involving the adjustment of schedules, setpoints, and control sequences, as opposed to more capi
1387 |  | Heat Pump Hot Water Heater | Energy Savings | 101.904 | 1158 |  |  |  |  | 0 | Analysis/Audit | The domestic hot water heater in the basement is a 40-gallon electric resistance water heater. Heat pump water heaters are much more efficient than electric resistance water heaters, and help dehumidify the surrounding space, which may negate the need for
1387 |  | Single Zone VAV Systems | Energy Savings | 642.4 | 7300 |  |  |  |  | 0 | Analysis/Audit | The air handling units serving the facility are currently constant volume systems with constant speed supply fans. This measure would convert the units to single zone variable air volume systems by installing variable frequency drives (VFDs) on the supply
1387 |  | Smart Pumps | Energy Savings | 195.127 | 1900 |  |  |  |  | 0.3 | Analysis/Audit
1387 |  | LED Lighting Upgrade | Energy Savings | 5796.75 | 39003 |  |  |  |  | 12.7 | Analysis/Audit | The existing lighting consists primarily of linear fluorescent fixtures with “Super” T8 (28-watt) lamps and high efficiency electronic ballasts. The main fixture types include 3-lamp 2’x4’ recessed troffers and wall-mounted linear fluorescent downlights.
1387 |  | Replace Aging Refrigerators | Energy Savings | 77.754 | 672 |  |  |  |  | 0.1 | Analysis/Audit | There are several refrigerators in kitchen areas throughout the facility. Electricity consumption for refrigerators is driven primarily by the size and age of the unit. Older refrigerators use much more energy than more modern energy efficient units. Whil
1387 |  | Plug Load Management | Energy Savings | 339.416 | 3857 |  |  |  |  | 0 | Analysis/Audit | Lighting and plug loads comprise the majority of the electric consumption in the office areas occupied by the State. There are a number of options for effectively managing plug loads, including the following: 1. Behavioral changes – Encourage building
1387 |  | LED Lighting Upgrade | Energy Savings | 181.72 | 2065 | 0 |  |  |  | 0.2 | Analysis/Audit | The existing lighting in office areas consists of a mix of surface mounted linear indirect T8 fixtures with “Super” T8 (28-watt) lamps and high efficiency electronic ballasts and suspended chandeliers with CFL bulbs. Basement areas have 3-lamp linear fluo
1387 |  | Variable Refrigerant Flow System | Energy Savings | -1035.056 | -11762 | 134 |  |  |  | 1 | Analysis/Audit | 116 State Street is not currently equipped with a central air conditioning system; space cooling needs are met using a total of ten (10) window air conditioners, with a total capacity of approximately 100,000 Btu/h, spread throughout the building. These w
1387 |  | Optimize Heat Recovery Unit Schedule | Energy Savings | 2011.152 | 22854 | 105.7 |  |  |  | 0 | Analysis/Audit | While most of the mechanical equipment operates according to schedules during normal building operation, there appears to have been a long-standing occupancy override in the building automation system for the heat recovery unit (HRU-1). HRU-1 provides 100
1387 |  | Optimize Hydronic Snowmelt Controls System | Energy Savings | 0 | 0 | 148.6 |  |  |  | 0 | Analysis/Audit | The building has a hydronic snowmelt control system that serves the front steps area. The snowmelt system utilizes the district steam and a heat exchanger to transfer heat to the glycol protected piping that serves the snowmelt zone. It was understood fro
1387 |  | Replace Aging Refrigerators | Energy Savings | 25.696 | 292 | 0 |  |  |  | 0.01 | Analysis/Audit | There is at least one full-size refrigerator in the building. This refrigerator appears to be an older vintage and because of that there may be an opportunity to reduce energy consumption with a newer refrigerator. Newer, ENERGY STAR refrigerators use les
1387 |  | Remedy Controls Issues | Energy Savings | 120.472 | 1369 | 0 |  |  |  | 0 | Analysis/Audit | During investigation of the building automation system, it was noticed that the heating hot water pumps P-3 and P-4 were commanded off, but their status was on. This is unusual unless the pumps have been left in ‘Hand’ mode however the pumps were set at 0
1387 |  | Rebalance Outdoor Airflow rates | Energy Savings | 114.048 | 1296 | 10.5 |  |  |  | 0 | Analysis/Audit | A survey of all the spaces in the building and use of the ASHRAE Standard 62.1 indicates the design outdoor airflow rate for the heat recovery unit (HRU-1) is somewhat oversized for the space ventilation requirements. HRU-1 is designed to provide 1,650 CF
1387 |  | Replace motors with Premium Efficiency Motors | Energy Savings | 77.88 | 885 | 0 |  |  |  | 0 | Analysis/Audit | Overall energy consumed by the fans and motors represents the largest electric energy use in the HVAC system for 116 State Street. Energy consumption could be reduced using premium efficiency motors for all fans and pump motors. Replacement motors could b
1387 |  | Smart Pump for Hot Water Systems | Energy Savings | 218.768 | 2486 | 0 |  |  |  | 0.4 | Analysis/Audit | Currently the building is equipped with two pairs of heating hot water pumps, one which serves hot water radiators throughout the building as well as a glycol hot water system which serves a heating coil in HRU-1. The existing pumps operate in a lead-stan
1387 |  | Replace R-22 Condensing Unit | Energy Savings | 629.024 | 7148 | 0 |  |  |  | 2.6 | Analysis/Audit | The heat recovery unit is equipped with a DX coil that is served by a condensing unit located in the attic. This condensing unit operates using refrigerant R-22, which is subject to phase-out implemented by the Montreal Protocol due to its negative enviro
1387 |  | Electric Snowmelt Control | Energy Savings | 1419.528 | 16131 | 0 |  |  |  | 0 | Analysis/Audit | 116 State Street has a steep, slate shingle roof, where the water is shed into gutters in four (4) locations, with a total of six (6) downspouts. The gutters and downspouts are equipped with electric snowmelt heat trace to ensure ice does not build up and
1387 |  | Lighting Controls Upgrade | Energy Savings | 70.488 | 801 | 0 |  |  |  | 0 | Analysis/Audit | The lighting in the building underwent a thorough lighting replacement in recent years that installed LED retrofit kits and LED bulbs throughout the building. However, the LED lights are still controlled by wall switches or circuit breakers, except for th
1387 |  | Multi Split AC System | Energy Savings | -1.084 | -3568 | 30 |  |  |  | 0 | Analysis/Audit | During the building walkthrough it was noted that there are several window air conditioning units that are installed to provide cooling to the building. These window AC units were not fully able to be identified during the walk through as some are install
1387 |  | Replace Refrigerator | Energy Savings | 24.288 | 276 | 0 |  |  |  | 0 | Analysis/Audit | There is one full-size refrigerator in the building. This refrigerator appears to be an older vintage and because of that there may be an opportunity to reduce energy consumption with a newer refrigerator. Newer, ENERGY STAR rated refrigerators use less e
1387 |  | Plug Load Management | Energy Savings | 27.104 | 308 | 0 |  |  |  | 0 | Analysis/Audit | Given the office occupancy of this building a large portion of its energy use can be attributed to plug loads. Items such as computers, printers, copies, monitors, phones, refrigerators, microwaves, coffeepots, etc. Many of these pieces of everyday office
1387 |  | LED Lighting Upgrade | Energy Savings | 11563.2903 | 89031 | 0 |  |  |  | 18.46 | Analysis/Audit | The existing lighting consist primarily of ceiling mount lensed fluorescent troffer fixtures with “Super” T8 lamps and high efficiency ballasts. While one floor of T8 fixtures have been replaced with LEDs in a couple of office areas, we recommend pursuing
1387 |  | Snowmelt Controls | Energy Savings | 203.4878 | 1622 | 0 |  |  |  | 0.3 | Analysis/Audit | 120 State Street has approximately 1,100 square feet of snowmelt serving the front walkway and steps to the building. This snowmelt system is served by a steam to hot water heat exchanger with a circulator pump. The snowmelt controls are not a packaged sy
1387 |  | Minimize Continuous Operation | Energy Savings | 4138.2288 | 9792 | 313 |  |  |  | 0 | Analysis/Audit | Based on a review of the electric meter interval data, we discovered that the building was placed in occupied mode 24/7 from early-January through April of 2019. This was put in place during a cold snap in order to prevent “losing” the building (i.e. not
1387 |  | Optimize BAS Schedules | Energy Savings | 3391.584 | 17364.5 | 177 |  |  |  | 0 | Analysis/Audit | While mechanical equipment operates according to schedules during normal building operation, there may be an opportunity for optimizing the occupied schedules to more accurately reflect actual building operating patterns. For example, many of the air hand
1387 |  | Reduce Exhaust Air Ventilation Rates | Energy Savings | 5581.9529 | 15521 | 376 |  |  |  | 1.4 | Analysis/Audit | The building ventilation requirements are served by constant flow exhaust fans and ducted outside air to the AHUs. These fans operate at a higher volume than the building needs and they are also enabled to run more often than necessary. A preliminary anal
1387 |  | Replace Steam Radiator Valves | Energy Savings | 1733.04 | 0 | 166 |  |  |  | 0 | Analysis/Audit | There are approximately 168 steam radiators that provide space heating to the building. Many of these steam radiators are equipped with aging and failing steam control valves. These steam control valves are being replaced when they are noticeably failed,
1387 |  | LED Lighting Upgrade | Energy Savings | 5998.974 | 50610 | 0 |  |  |  | 8.3 | Analysis/Audit | The existing lighting consists primarily of T5 linear fluorescent fixtures. We recommend pursuing a comprehensive LED lighting upgrade to replace the existing fixtures. Along with the benefit of lower wattage compared to fluorescents, LED lamps also have
1387 |  | Heat Pump Hot Water Heater | Energy Savings | 167.2 | 1900 |  |  |  |  | 0 | Analysis/Audit | The domestic hot water heater in the basement is a 40-gallon electric resistance water heater. Heat pump water heaters are much more efficient than electric resistance water heaters and help dehumidify the surrounding space. For the type of domestic hot w
1387 |  | Refrigerator Replacement | Energy Savings | 28.2618 | 300 |  |  |  |  | 0.01 | Analysis/Audit | There is a refrigerator in the main office area. Electricity consumption for refrigerators is driven primarily by the size and age of the unit. Older refrigerators can use much more energy than more modern energy efficient units. When the existing refrige
1387 |  | LED Lighting Upgrade | Energy Savings | 391.9851 | 2326 | 0 |  |  |  | 1.006 | Analysis/Audit | The existing lighting consists primarily of linear fluorescent and compact fluorescent (CFL) fixtures. Linear fluorescent fixtures have T8 lamps and high performance electronic ballasts (“Super T8s”). We recommend pursuing a comprehensive LED lighting upg
1387 |  | Optimize Occupancy Schedules and Setpoints | Energy Savings | 109.758 | 0 | 6.6 |  |  |  | 0 | Analysis/Audit | Currently the occupancy schedule for the building implemented in the BAS is weekdays 5:00 a.m. – 6:30 p.m, and the unoccupied heating temperature setpoint is 68°F., This unoccupied setpoint is actually higher than the occupied setpoint in several of the z
1387 |  | Energy Recovery Ventilator | Energy Savings; IAQ | 249.3932 | 166 | 9.64 |  |  |  | 0.8 | Analysis/Audit | Currently the only mechanical ventilation being provided to the building is through bathroom exhaust fans, which only operate intermittently. Given what we know regarding the increased importance of ventilation, especially during COVID-19, we recommend in
1387 |  | Band Joist Insulation | Energy Savings | 434.043 | 0 | 26.1 |  |  |  | 0 | Analysis/Audit | The majority of the basement walls appeared to have been insulated at one time with 6.5-inch fiberglass batts and covered with a plywood sheathing. The effectiveness of some of it is questionable as much of it is separated by a relatively large air space,
1387 |  | Upper Attic Insulation & Air Sealing | Energy Savings | 405.772 | 0 | 24.4 |  |  |  | 0 | Analysis/Audit | The upper most attic cap has 4 to 5 inches of blown-in mineral wool insulation. While this does provide some thermal resistance, the fact that the insulation has been compressed over many years, combined with the lack of air sealing of the attic floor, ma
1387 |  | Miscellaneous Air Sealing | Energy Savings | 146.344 | 0 | 8.8 |  |  |  | 0 | Analysis/Audit | The following discussions pertain to several common types of air leakage that, cumulatively, have an appreciable impact on energy consumption. Therefore, we put them together into one “catch-all” measurement for improvement. Window Trim Because the
1387 |  | Level 3 South Insulation & Air Sealing | Energy Savings | 508.878 | 0 | 30.6 |  |  |  | 0 | Analysis/Audit | South of the level 3 stairwell, the storage space has R19 foil-faced fiberglass batts on the slopes and R11 foil-faced fiberglass batts on the gable end. The batts are not in terrible shape, but the R-value present is relatively low for a roof and wall, a
1387 |  | Level 3 North Insulation & Air Sealing | Energy Savings | 701.786 | 0 | 42.2 |  |  |  | 0 | Analysis/Audit | In general, the walls on level 3 look like they are relatively well insulated in the stairwell, similar to level two, but the roof slopes and dormer walls of the northern end (north of the stairwell) are poorly insulated with blown-in mineral wool. Much o
1387 |  | Window Replacement | Energy Savings | 1134.166 | 0 | 68.2 |  |  |  | 0 | Analysis/Audit | Most of the windows in the building are wood frame, single-hung, single-pane windows with weighted pulleys and an exterior storm. The wood frame windows, after so many years of wear and tear, do not create a tight air seal when closed, and the single pane
1387 |  | Heat Pump Hot Water Heater | Energy Savings | 38.192 | 434 | 0 |  |  |  | 0 | Analysis/Audit | The domestic hot water heater in the basement is a 30-gallon electric resistance water heater. This unit was installed in 2012, so it may not make sense to replace it at this time. We recommend installing a heat pump water heater when the existing unit f
1387 |  | Smart Pumps for Hot Water Circulators | Energy Savings | 106.618 | 1000 | 0 |  |  |  | 0.2 | Analysis/Audit | Currently the building is equipped with five (5) constant speed 1/25 hp heating hot water circulator pumps, which circulate hot water to the five zones in the building. Modern pumps are coming equipped with ECM motors, ‘smart’ controls to vary the flow
1387 |  | LED Lighting Upgrade | Energy Savings | 365.8208 | 2126 | 0 |  |  |  | 0.96 | Analysis/Audit | The existing lighting consists primarily of suspended pendants and chandeliers with a mixture of screw-in compact fluorescent and LED lamps. There are also some linear fluorescent fixtures with “Super” T8 lamps and high efficiency electronic ballasts in t
1387 |  | Add Insulation Jacket to Main Steam Valve | Energy Savings | 184.593 | 0 | 11.1 |  |  |  | 0 | Analysis/Audit | While the steam piping appears to be generally well insulated, there is an opportunity to insulate the main steam shutoff valve. We recommend installing a removable insulation jacket for the 8” gate valve. These jackets are easy to install and typically c
1387 |  | Heat Pump Clothes Dryer | Energy Savings | 315.804 | 1473 | 0 |  |  |  | 1 | Analysis/Audit | The electric clothes dryer in the basement is used a few hours a day by BGS staff to dry laundry. We recommend installing a heat pump clothes dryer, which uses 2-3 times less electricity than typical electric vented dryers. We recommend procuring a heat p
1387 |  | Plug Load Management | Energy Savings | 64.653 | 523.125 |  |  |  |  | 0.1 | Analysis/Audit | Plug loads are estimated to comprise over 20% of the electricity consumption at the building. There are a number of options for effectively managing plug loads , including the following: 1. Behavioral changes – Encourage building occupants to power dow
1387 |  | Energy Recovery Ventilator | Energy Savings; IAQ | 560.081 | 450 | 25.7 |  |  |  | 2 | Analysis/Audit | Currently the only mechanical ventilation being provided to the building is through bathroom exhaust fans, which only operate intermittently. Given what we know regarding the increased importance of ventilation, especially during COVID-19, we recommend in
1387 |  | Window Replacement | Energy Savings | 1320.422 |  | 79.4 |  |  |  |  | Analysis/Audit | Most of the windows in the building are wood frame, single-hung, single-pane windows with an exterior storm window. The wood frame windows, after so many years of wear and tear, do not create a tight air seal when closed, and the single pane of glass offe
1387 |  | Door Weather Stripping | Energy Savings | 104.769 |  | 6.3 |  |  |  |  | Analysis/Audit | Air leakage was observed around all of the exterior doors in the building. On doors that are still in good shape, the most cost-effective measure is to check the thresholds, sweeps, and weather-stripping once a year and replace as needed. Even old doors
1387 |  | Interior Air Sealing | Energy Savings | 262.754 |  | 15.8 |  |  |  |  | Analysis/Audit | Because the only true air barrier in the building is the interior plaster walls, wherever the plaster meets another material, there is a possibility that air leakage will occur at that transition or where the interfacing material transitions to another ma
1387 |  | Insulate Basement Walls | Energy Savings | 786.599 |  | 47.3 |  |  |  |  | Analysis/Audit | The basement walls appeared to have been insulated at one time with 3.5-inch fiberglass batts and covered with a plywood sheathing. However, most of the insulation has now been removed, and whatever remains is ineffective because it is not properly contac
1387 |  | Seal Fireplaces | Energy Savings | 236.146 |  | 14.2 |  |  |  |  | Analysis/Audit | There are four fireplaces: two on the first floor and two on the second floor. The fireplaces on the first floor have been stuffed with fiberglass insulation and infilled with a plywood cover. While this does provide some thermal resistance, there was evi
1387 |  | LED Lighting Upgrade | Energy Savings | 15078.1224 | 102753 | 0 |  |  |  | 24.7 | Analysis/Audit | The existing lighting in office areas consists primarily of suspended linear indirect T8 fixtures with “Super” T8 (28-watt) lamps and high efficiency electronic ballasts. Basement areas have 3-lamp linear fluorescent 2’x4’ recessed troffers. Corridors hav
1387 |  | Minimize 24/7 Building Operation | Energy Savings | 9503.8971 | 64114 | 319 |  |  |  | 0 | Analysis/Audit | Based on a review of the electric meter interval data and discussion with facilities staff, we discovered that the building was placed in occupied mode 24/7 from mid-January through April. This was put in place during a cold snap in order to prevent “losi
1387 |  | Optimize BAS Occupancy Schedules | Energy Savings | 2405.7697 | 13275 | 108 |  |  |  | 0 | Analysis/Audit | While mechanical equipment operates according to schedules during normal building operation, there may be an opportunity for optimizing the occupied schedules to more accurately reflect actual building operating patterns. For example, many of the floors a
1387 |  | Reduce Outside Air Ventilation Rates | Energy Savings | 7299.3938 | 38020 | 55 |  |  |  | 14.6 | Analysis/Audit | The large energy recovery unit (ERU-1) in the mechanical penthouse supplies 100% outside air for ventilation for building occupants. A preliminary analysis of current outdoor air ventilation rates indicates excessive ventilation air is being provided base
1387 |  | Optimize FCU Operation | Energy Savings | 1220.0397 | 8854 | 35.2 |  |  |  | 0 | Analysis/Audit | There are over two hundred fan coil units serving spaces in the building, with temperature setpoints ranging from 65°F to 76°F. While most (~80%) of these are operating in AUTO mode, the remainder have the fan running whenever the unit is in occupied mode
1387 |  | ECM Motors for FCUs | Energy Savings | 7409.0193 | 36839 |  |  |  |  | 18.4 | Analysis/Audit | Brushless DC motors, also known as electronically commutated (ECM) motors, are significantly more efficient than standard permanent split capacitor (PSC) motors and are an ideal application for fan coil units. While retrofitting all of the FCUs with new E
1387 |  | Differential Pressure Reset | Energy Savings | 1094.9136 | 11371 |  |  |  |  | 0 | Analysis/Audit | The hot water and chilled water pumps currently operate to maintain fixed differential pressure setpoints in their respective loops. While this setpoint may be appropriate for periods when maximum heating or cooling is required, the setpoint can be reset
1387 |  | Run Cooling Tower Fans in Parallel | Energy Savings | 603.2568 | 6265 | 0 |  |  |  | 0 | Analysis/Audit | The cooling tower fans are variable speed and controlled with VFDs to maintain the leaving tower condenser water temperature at setpoint. Due to the nature of the fan affinity laws, whereby fan power is proportional to the cube of the fan speed, it is alw
1387 |  | Plug Load Management | Energy Savings | 1631.5406 | 16944.03 | 0 |  |  |  | 0 | Analysis/Audit | Analysis of the electric meter interval data revealed that there is a relatively high nighttime unoccupied baseload of around 90 kW. While it is unclear what exactly is contributing to this load, plug loads such as computers, monitors, and copiers are oft
1387 |  | Chiller Replacement | Energy Savings | 6747.3025 | 48712 | 0 |  |  |  | 19.6 | Analysis/Audit | The chilled water plant consists of three (3) chillers with a total capacity of 250 tons. While these were relatively efficient at the time they were installed in 2003, chiller technology has advanced significantly over the past fifteen years, especially
1387 |  | LED Lighting Upgrade | Energy Savings | 30002.9359 | 232861 |  |  |  | -2140.3205 | 40.2 | Analysis/Audit | The existing lighting fixture types in the facility varies based on the use of the space and if the occupancy is intended for the inmate population or for the staff. The lighting fixtures primarily use 25-watt “Super” T8 fluorescent lamps and electronic b
1387 |  | Optimize BAS Occupancy Schedules | Energy Savings | 18525.6887 | 83012 |  |  |  | 9770 | 0 | Analysis/Audit | Currently all of the air handling units serving the facility are in occupied mode 24/7. While this is necessary for many areas such as the inmate housing units and infirmary, there are other areas that most likely do not require 24/7 operation. This measu
1387 |  | Single Zone VAV Systems | Energy Savings | 3586.3877 | 36788 |  |  |  | 0 | 0 | Analysis/Audit | For the single zone AHUs, install VFDs on the supply and return fans and operate the units as single zone variable air volume (VAV) systems under automatic control. This will allow the fan speeds to be reduced during low load periods, resulting in substan
1387 |  | Efficient Washing Machines | Energy Savings | 4180.3474 | 6454 |  |  |  | 3516 | 0 | Analysis/Audit | Currently, the facility uses top-load washing machines which consume approximately 20-gallons of water per cycle. According to the washing machine identified in the infirmary, these units have a 3.3ft3 tub capacity. This style washing machine uses more wa
1387 |  | Solar Hot Water | Energy Savings | 9626.9817 | -4300 |  |  |  | 10252 | -1.5 | Analysis/Audit | One of the largest loads on the steam system is the domestic hot water system. All domestic hot water is provided by steam-to-hot-water heaters. There is a large domestic hot water load at the facility due to showers, laundry, and kitchen end uses. The op
1387 |  | Demand Control Kitchen Ventilation | Energy Savings | 11185.6946 | 26391 |  |  |  | 8185 | 0 | Analysis/Audit | Currently the kitchen exhaust hood fan (EF-9G) and associated makeup air unit (MUA-1G) supply fan run at a constant speed whenever the hood is turned on and operating. The kitchen exhaust hood fan removes smoke and combustion byproducts created during coo
1387 |  | Refrigeration Upgrade | Energy Savings | 4402.0076 | 28396 |  |  |  | 0 | 4.75 | Analysis/Audit | All of the refrigeration equipment serving the kitchen is original to the building and may be approaching the end of its useful life. Additionally, the condensing units serving the walk-in coolers use R-22 refrigerant, which can no longer be produced or i
1387 |  | Energy Efficient Transformers | Energy Savings | 10788.6698 | 84516 |  |  |  | 0 | 9.6 | Analysis/Audit | Since the facility electric meter is located on the primary side of the building transformers, the transformer losses directly impact the metered electric consumption. While transformers are very efficient devices, since they are always operating, even a
1387 |  | 'Smart' Pump for Heating Hot Water System | Energy Savings | 177.471 | 773 |  |  |  | 0 | 0.38 | Analysis/Audit | Currently the core facilities building is equipped with a heating hot water pump which serves hot water reheat coils throughout the facility. The existing pumps operate in a lead-standby configuration where only one pump operates at a time. The current pu
1387 |  | Building-Level Electric Submeters | O&M | [7 empty] | Analysis/Audit | Currently, there is one electric meter serving the entire campus of seven buildings. Installing electric submeters for each building would allow for more granular data collection and analysis. Benchmarking could be performed for each individual building,
1387 |  | Steam Meters | O&M | [7 empty] | Analysis/Audit | Installing steam meters in various locations can yield insight into the operation of the steam system and help direct maintenance activities. For example, a meter located where the steam leaves the energy building can allow for the calculation of the boil
1387 |  | Steam Trap Survey and Assessment | Energy Savings; O&M | [7 empty] | Analysis/Audit | Steam traps can have a failure rate of 15-20% annually, resulting in increased energy consumption if failed open as the trap constantly passes steam. We recommend conducting a survey of all steam traps in the facility and implementing an annual steam trap
1387 |  | Testing, Adjusting, and Balancing (TAB) | Energy Savings; IAQ; O&M | [7 empty] | Analysis/Audit | During the energy audit, facilities staff indicated that the mechanical systems would be undergoing testing, adjusting, and balancing (TAB) sometime in the next year. We strongly recommend that this be done, as properly balanced systems can result in redu
1387 |  | Refrigeration Condensing Coil Maintenance | O&M | [7 empty] | Analysis/Audit | We did not examine all of the condensing coils for refrigeration equipment and facility staff may already be including this in their preventive maintenance activities. We recommend cleaning coils quarterly and ensuring there is sufficient clearance for ad
1387 |  | Repair Condensate Meter | O&M | [7 empty] | Analysis/Audit | The building is equipped with a condensate meter to measure steam consumption, but historical data was not available. We recommend repairing any issues that are preventing the metering and collection of this data. Accurate metering can help establish a ba
1387 |  | Direct Digital Controls Upgrade | Energy Savings; O&M | [7 empty] | Analysis/Audit | The building currently uses pneumatic actuators to control valves and dampers, which has air supplied by a compressor located in the basement. Electropneumatic transducers are used to translate the control signal from the BAS to the proper air pressure. R
1387 |  | Ducted Outdoor Air and Return Air | Energy Savings; IAQ | [7 empty] | Analysis/Audit | Currently the attic serves as a return plenum for AHU-2 and AHU-3. Air is returned from the spaces served by these units directly into the attic, and is drawn into the AHUs along with some amount of outdoor air that enters through the louvers on the walls
1387 |  | Ensure Building Energy Meters are Calibrated and Operating Properly | [8 empty] | Analysis/Audit | There are issues with the building-level condensate meter resulting in gaps in data, causing evaluators to rely on estimations for whole-building energy consumption. To establish an effective energy management program, it is essential that energy meters
1387 |  | Ensure Building Energy Meters are Calibrated and Operating Properly | O&M | [7 empty] | Analysis/Audit | There were issues with the building-level electric and condensate meters resulting in gaps in data and estimates for whole-building energy consumption. To establish an effective energy management program, it is essential that energy meters are calibrated
1387 |  | Steam Trap Survey and Assessment | Energy Savings; O&M | [7 empty] | Analysis/Audit | We spot checked a couple of steam traps while on site, and they appeared to be operating properly. Since steam traps typically have a relatively high failure rate, we recommend conducting a survey of all steam traps in the facility and implementing an ann
1387 |  | Engage Occupants Regarding Electric Space Heaters | Energy Savings; O&M | [7 empty] | Analysis/Audit | We observed a number of electric space heaters in many of the offices, and electric meter data showed significantly higher consumption during the winter months. Occupant thermal comfort is the most important service a building provides, but we encourage B
1387 |  | Repair Electric and Condensate Meters | O&M | [7 empty] | Analysis/Audit | the building is equipped with an electric sub-meter and condensate meter, but historical data was not available. We recommend repairing any issues that are preventing the metering and collection of this data. Accurate metering can help establish a baselin
1402 |  | Chilled Water Suply Reset | Energy Savings | 3377 | 23764 | [5 empty] | Retrocommissioning | The chillers provided a constant 43°F supply water temperature. While this may be necessary during days with high ambient temperature and humidity, this temperature is unnecessarily low when temps and especially humidity are lower. By increasing the CHW t
1402 |  | Chilled Water Loop DP Reset | Energy Savings | 5363 | 37740 | [5 empty] | Retrocommissioning | The 15-hp chilled water secondary pumps (P-7 and P-8), while served by VFDs, do not significantly vary speed throughout the year. See Figure 3. This indicates that while the hardware is in place in the central plant to provide variable speed pumping, much
1402 |  | Chilled Water Dry Cooler | Energy Savings | 7557 | 53180 | [5 empty] | Retrocommissioning | During the shoulder and winter months, there are many hours when the chiller is operating, but outdoor air conditions are favorable for free cooling by a dry cooler—basically a radiator, like the one in place for GMC’s emergency generator. We plotted the
1408 |  | Condneser Water Reset Schedule | Energy Savings | 1175 | 6850 | [5 empty] | Retrocommissioning | The current return water setpoint is 85°F. We recommend implementing a reset schedule that adjusts this setpoint to the minimum condenser water temperature required by the chillers based on outside air wetbulb temperature. This will increase the run time
1408 |  | Cooling Tower Fan Sequencing | Energy Savings | 1000 | 5500 | [5 empty] | Retrocommissioning | Currently the cooling tower fan sequence operates 1 cell with 1 fan and no spray pump in a lead/lag fashion. In winter, maintenance staff need to manually chop ice and sweep snow off before they start the fan due to ice buildup. The control sequence could
1408 |  | Chiller Supply Temp Reset Schedule | Energy Savings | 2325 | 13700 | [5 empty] | Retrocommissioning | The chilled water supply temperature setpoint is 45°F, but Dan Rich stated that the building can handle a setpoint of 50°F for all times except for some very high temp/humidity days. We suggest programming the BAS to operate the chillers with a reset sche
1412 |  | Building tap | Energy Savings | 66848 | 66683 | [5 empty] | Retrocommissioning
1413 |  | SAT Reset | Energy Savings | 1194 | 0 | [5 empty] | Commissioning | None of the building air handlers were observed to have a programmed supply air temperature sequence. SAT setpoints minimize energy use and relieve a burden offf of facility staff. Aimplementing a supplu air temperatrue reset reduced both AHU cooling and
1414 |  | SASP Reset | Energy Savings | 1270 | 8536 | [5 empty] | Commissioning | AHU 1 through 3 are air handlers with terminal VAV systems and utilize a static pressure setpoint to maintain airflow at VAVs. Implementing a static pressure setpoint will decrease fan speed and fan energy consumption by allowing the static setpoint to be
1415 |  | Valve/Damper Control | Energy Savings | 329 | 2029 | [5 empty] | Commissioning | BAS review idnetified several issues with AHU dampers, heating and cooling valve positions. These cause operational problems such as deadheading a fan and can increase energy consumption by simultaneously heating and cooling at the air handler. implementi
1416 |  | Pump DP Reset | Energy Savings | 1630 | 10954 | [5 empty] | Commissioning | Currently both hot and chilled water secondary loop pump speeds are controlled to maintain a constant differential pressure setpoint. Implementing a DP setpoint reset strategy will reduce the setpoint duirng part load conditions, thus allowing the pumps t
1417 |  | HW Temp Reset | Energy Savings | 6797 | 0 | [5 empty] | Commissioning | There is currently a secondary hot water temperature setpoint reset programmed to lower the hot water temperature when the outside air temperature increases. While this method works, it is not as effective at increasing efficiency as resetting the hot wat
1418 |  | Boiler Efficiency | Energy Savings | 7552 | 0 | [5 empty] | Commissioning | The condensing boilers, installed in the building, are designed to achieve their peak efficiency rating of 98% when they operate with condensing flue gas. For flue gas to condense, return water temperatures must be below 135°F and the boiler does not reac
1419 |  | DHW Pump Operation | Energy Savings | 162 | 1089 | [5 empty] | Commissioning | It was observed during the BAS review that both DHW pumps were on at the same time although one pump was commanded off. These pumps are designed to operate in a lead/lag fashion, where one operates while the other serves as a backup in the case of a lead
1420 |  | CHWT Reset | Energy Savings | 417 | 2804 | [5 empty] | Retrocommissioning | The existing chilled water system cools water to a manually input setpoint.This setpoint is changed by Spruce Camp staff depending on outside air conditions to meet the cooling demand of the building. The chiller will operate more efficiently as the tempe
1421 |  | CWST Reset | Energy Savings | 417 | 2804 | [5 empty] | Problem Solving | The condenser water temperature setpoint can be reset based on outside air temperature to maximize the chiller operating efficiency. Lowering the condenser water supply temperature automatically, when outside air conditions allow, will help increase chill
1422 |  | VAV Unocc. Operation | Energy Savings | 1194 | 0 | [5 empty] | Problem Solving | The BAS review showed that VAV-2-15 has an unoccupied space heating temperature setpoint that conflicts with the occupied setpoint; namely, the occupied setpoint is below the unoccupied setpoint.Typically, unoccupied heating setpoints are a minimum of 5°F
1423 |  | MAU-1/2 Operation | Energy Savings | 1194 | 0 | [5 empty] | Commissioning | MAU-1 and MAU-2 are designed to provide makeup air to the kitchen exhaust hoods. During review of the BAS, it was found that MAU-2 was not in operation when its associated kitchen exhaust hoods were in operation, and that MAU-1 was only operating at ~900C
1424 |  | VFD Integration | Energy Savings | 0 | 0 | [5 empty] | Retrocommissioning | Spruce Camp staff noted that not all of the existing variable frequency drives have been integrated into the BAS graphics as there were specified to be. This leaves several drive displays on the BAS without valuable energy and operating data that could be
1425 |  | Snowmelt HX Bypass | Energy Savings | 3704 | 2214 | [5 empty] | MEP Cx | The current design of the hot water piping system requires return heating hot water to flow through the heat exchanger for the snowmelt system, even when the snowmelt system is not active. This heat exchanger adds pressure drop to the system, which requir
1426 |  | Snowmetl Controls (prelim) | Energy Savings | 4048 | 0 | [5 empty] | MEP Cx | Spruce Camp described issues with the snowmelt system during large snowstorms. At these times, a majority of the heating capacity is diverted to the snowmelt system and the hot water system cannot meet the building loads. This could be due to the system n
1430 |  | Optimize BAS Scheduling | Energy Savings | 1273 | 13208 | [5 empty] | Retrocommissioning | The existing BAS schedule for the occupied mode is from 6:00 a.m. to 9:00 p.m. seven days a week. Based on discussions with building occupants and facility staff, these operating hours are longer than needed. Tightening the building operating schedule wou
1430 |  | Shut Down ERV-1 During Unoccupied Hours | Energy Savings | 774 | 8141 | [5 empty] | Retrocommissioning | .Currently the main energy recovery unit serving the building (ERV-1) does not shut down completely during unoccupied periods, but instead runs at its minimum speed. This operation was initially put in place to address issues with stale smells in the buil
1430 |  | Reduce Exhaust Fan Speed During Unoccupied Hours | Energy Savings | 126 | 1429 | [5 empty] | Retrocommissioning | The relatively new exhaust fan serving the toilet and janitor areas currently runs continuously 24/7 at 100% speed. This measure reduces the fan speed during unoccupied hours while bathroom and janitor area use is expected to be minimal or nonexistent. B
1430 |  | Increase CO2 Level Setpoints | Energy Savings | 167 | 1151 | [5 empty] | Retrocommissioning | Currently the CO2 level setpoint is set to 900 ppm, above which VAV boxes will modulate open to introduce more ventilation air and cause ERV-1 fan speeds to increase. This setpoint could be raised to 1,100 ppm, which would be consistent with the UVM stand
1430 |  | Run Fan Coil Units in Cycle Mode | Energy Savings | 886 | 10069 | [5 empty] | Retrocommissioning | The fan coil units can run in either “Cycle” or “FAN ON” mode, and it is estimated that many of the units are currently manually operating in “FAN ON” mode, in which the fan operates continuously when the spaces are occupied. In “Cycle” mode, the fan only
1430 |  | Optimize Control of HRV-1 | Energy Savings | 503 | 5716 | [5 empty] | Retrocommissioning | The heat recovery ventilator serving the eco-machine room currently runs continuously 24/7. This measure shuts this unit off during unoccupied hours. Since there is hot water baseboard radiation serving this area, the HRV is not required and the baseboard
1430 |  | Optimize Control of Pumps CP-7/CP-8 | Energy Savings | 663 | 7534 | [5 empty] | Retrocommissioning | During our building walk-through, we discovered that pump CP-8 was running, which serves the 4-pipe fan coil unit chilled water loop, even though there was no cooling requirement at the time in the spaces served. Facilities staff then informed us that thi
1431 |  | Exhaust Fans VFD | Energy Savings | 4000 | 4500 | [5 empty] | Retrocommissioning | The current exhaust fans operate on a constant static pressure and modulate the outside air damper within the plenum. By installing a VFD on the existing fans, the outside air bypass can be removed, and the fans will only exhaust fume hood air. The fans c
1431 |  | Replace 3-way Valves | Energy Savings | 1100 | 3500 |  |  | 150 |  |  | Retrocommissioning | The existing 3-way valves at the VAV boxes prohibit the hot water pump from modulating to meet actual conditioning loads. The constant recirculation of the hot water also increases the return water to the boiler and prohibits the boiler from operating in
1431 |  | Min/Max Space Temperatures | Energy Savings | 1740 | 3650 |  |  | 600 |  |  | Retrocommissioning | If the laboratory end-use processes will allow it, we recommend implementing a min/max range for each space thermostat so that the spaces do not have large extremes and the building reduces its simultaneous heating and cooling. During our site visit, one
1431 |  | Night Setback/up Temperatures | Energy Savings |  | 4870 | [5 empty] | Retrocommissioning | The current nighttime unoccupied setpoint is 63°F. Unless the ecological processes cannot accept lower temperatures, we recommend lowering this temperature to 60°F for all appropriate spaces (assumed to be 80% of the building for the savings calculations)
1431 |  | Shut off Heat Pump | Energy Savings |  | 3150 | [5 empty] | Retrocommissioning | One (of a total of two) heat pump remains operating but we could not trace where this unit is serving. There is a large possibility the spaces were reconfigured, and this unit is no longer necessary. UVM can consider turning the unit off and determining i
1431 |  | Test HVAC Occupancy Sensors | Energy Savings |  | 3700 | [5 empty] | Retrocommissioning | This unoccupied demand seems high and may be indicative of malfunctioning HVAC occupancy sensors that do not enable the VAV boxes to go to the lower airflow. This would increase the ERV, chiller, boiler demands unnecessarily. We recommend trending the VAV
1471 |  | AII Room Exhaust/Return NMC AHU | Code / Safety | [7 empty] | MEP Cx | AII rooms were designed with an optional "Patient Mode" where air from the room could be returned to the AHU, which doesn't meet our interpretation of the ASHRAE 170 code. Moving forward with the design in place may have resulted in the new spaces not be
1482 |  | Reduce Cooling Tower Pump Minimum Speed | Energy Savings | 250 | 3900 |  |  | 0 |  | 0 | Retrocommissioning
1482 |  | Relocate/Calibrate BAS Outside Air Temperature Sensor | Energy Savings | 3850 | 250 |  |  | 0 |  | 0 | Retrocommissioning
1482 |  | Install VFD on the supply and return fans of MUA#2 | Energy Savings | 850 | 24700 |  |  | 0 |  | 0 | Retrocommissioning
1482 |  | Replace garage light bulbs with LED bulbs | Energy Savings | 3500 | 4900 |  |  | 0 |  | 0 | Retrocommissioning
1498 |  | Controls programming and sensor calibration | Energy Savings | 3825 | 11085 |  |  | 1505 |  | 0 | Retrocommissioning
1498 |  | Maintenance | Energy Savings | 2650 | 3325 |  |  | 1505 |  | 0 | Retrocommissioning
1498 |  | Boiler piping and DHW analysis | Energy Savings | 1725 | 0 |  |  | 1204 |  | 0 | Retrocommissioning
1499 |  | Differential Pressure Reset on HWP-3 and HWP-4 | Energy Savings | 992 | 6610 | [5 empty] | Retrocommissioning | HWP-3 and HWP-4 are the secondary pumps, which circulate hot water throughout most of the building. They have VFDs and their speed is controlled to maintain a fixed 7 PSI differential pressure (dP) setpoint. This measure would reset the dP setpoint based
1499 |  | Reprogram Unit Ventilator Fan and Valve Control | Energy Savings | 566 | 3085 | [5 empty] | Retrocommissioning | At night, the Unit Ventilators throughout the building often go into heating mode, which opens the hot water valves 100% but does not turn on the fan (eventually the fan turns on). This measure involves reprogramming the units so that when the zone calls
1499 |  | AHU-1 and AHU-2 Demand Controlled Ventilation | Energy Savings | 414 | [6 empty] | Retrocommissioning | AHU-1 and AHU-2 have a fixed minimum outside air damper position. This means that whenever the units are on, they bring in outside air even if the spaces are empty. This measure would involve using the CO2 sensor as an indication of occupancy, and adjusti
1499 |  | AHU-1 and AHU-2 Minimum Fan Speed Adjustment | Energy Savings | 59 | 394 | [5 empty] | Retrocommissioning | The AHUs have a minimum fan speed of 50%. When the units are heating, this is likely necessary in order to properly mix the air in the space and prevent warm supply air from stratifying and staying near the ceiling. However, when the AHU is not heating or
1499 |  | Holiday Setback Schedules | Energy Savings | 1328 | 3338 | [5 empty] | Retrocommissioning | The ALC control system is capable of incorporating holiday schedules. While on site, Josh Dalmer showed the staff the scheduling features of ALC. We recommend a quick training for all staff. We also recommend assigning holiday scheduling to a staff member
1499 |  | Optimal Start/Stop Fine Tuning | Energy Savings | 554 | [6 empty] | Retrocommissioning | Optimal Start/Stop is a control feature that uses historical trend data from outdoor and indoor temperatures to determine the appropriate equipment start time prior to a building’s occupied mode. The idea is that on a cold morning, it will start the equip
1499 |  | Storage Room 100 (FTR-1) Temperature Setpoint and Control | Energy Savings | 41 | 394 | [5 empty] | Retrocommissioning | The storage room is unoccupied most of the time and unless sensitive supplies are stored there, the space temperature setpoint (both occupied and unoccupied) could be lowered. In addition, the fan coil heater frequently turns on for 3 minutes (about 100 f
1499 |  | Vestibule 101 Radiant Heating | Energy Savings | 103 | 83 | [5 empty] | Retrocommissioning | Currently, the radiant heat is disabled when the outside air temperature exceeds 65°F. It could likely be locked out at a lower temperature, perhaps 50°F or 55°F. In addition, if people are not spending much time in the vestibule, it could likely be heate
1499 |  | AHU-1 and AHU-2 Supply Air Temperatrure Control | Energy Savings | 163 | [6 empty] | Retrocommissioning | AHU-1 and AHU-2 use the room temperature PID loop to directly control the heating valve. One challenge with this type of control is that it does not easily allow us to maintain the temperature within a specific range. Trends indicate that supply air tempe
1499 |  | Ahu-1 and AHU-2 Nighttime VFD Speed and HHW Control Valve | Energy Savings | 33 | 417 | [5 empty] | Retrocommissioning | At night, when these units turn on, they go to 100% speed and 100% valve position immediately. This allows them to quickly heat the space, but they only run about 5 minutes and often turn on about 10 times each night. With such a short run time, the air l
1499 |  | Unoccupied Heating Setpoints | Energy Savings | 207 | 394 | [5 empty] | Retrocommissioning | The building sets back the heating temperature setpoint throughout the building. There may be opportunity to set the temperature back more in some spaces. Currently, most spaces heat to 65°F at night. That is probably appropriate for rooms that are slow t
1499 |  | Cabinet Unit Heaters Tuning | Energy Savings | 166 | 881 | [5 empty] | Retrocommissioning | Some of the cabinet unit heaters appear to be short cycling. The fan in CUH-2 appears to only run for 1 minute when it turns on. When the HHW valve opens, it goes to 100% and also only stays open briefly. We recommend checking the PID parameters and consi
1499 |  | HWP-1 Enable Setting | Energy Savings | 59 | 441 | [5 empty] | Retrocommissioning | HWP-1, which circulates water through the heat exchanger on the building side, enables when outside air temperature is less than 65°F. The building appears to have little to no heating needs when outside air temperature is ~60°F. This measure would involv
1499 |  | Access Additional Hot Water Piping Configurationi | Energy Savings | 132 | 1902 | [5 empty] | Retrocommissioning | The piping in the addition has equipment from various ages and serves both heating and domestic hot water loads. There appear to be multiple bypasses in the system between the district heat and the end uses in the addition. This measure would trace out th
1499 |  | Cafeteria AHU Heat Coil Valve | Energy Savings | 273 | 394 | [5 empty] | Retrocommissioning | The Cafeteria AHU has face and bypass control and does not have any control valve for the hot water coil. Hot water is always flowing through the coil. When the AHU is heating, air is diverted through the coil. When the AHU does not need to heat, air is d
1499 |  | Exhaust Fans Integrated into BAS | Energy Savings | 389 | [6 empty] | Retrocommissioning | The building has several (about 5-8 exhaust fans), but only EF-4, the kitchen exhaust fan, the auditorium exhaust fan, and the gym exhaust fan are integrated with the BAS. This measure would investigate the other exhaust fans and what they serve. If they
1499 |  | Gym and Small Gym Motion Sensors | Energy Savings | 163 | 3333 | [5 empty] | Retrocommissioning | The gym and small gym have motion sensor for lights. This measure would investigate integrating the motion sensors into the BAS. Then the sequence would be modified so that if the space was empty during normal occupied, the AHU could be put into a standby
1499 |  | Distric Heat Bills | Energy Savings | [7 empty] | Retrocommissioning | MRPS staff noted that the district heat bills are quite high for this building compared to other MRPS buildings that heat with fuel oil. It is possible that there could be billing errors. This measure would investigate the district heat bills. We would ch
1499 |  | District Heat Minimum Valve Postion and Minimum VFD Speed | Energy Savings | [7 empty] | Retrocommissioning | We understand from TCV that when the controls were set up, the district heat operators wanted to maintain a particular return water temperature and a minimum flow rate. On the district side of the heat exchangers, there is a control valve that normally ha
1499 |  | Replace HWP-1 and HWP-1 With Smartpumps | Energy Savings | 500 | [6 empty] | Retrocommissioning | HWP-1, HWP-2, HWP-3, and HWP-4 all serve a similar function but while HWP-3 and HWP-4 have VFDs, HWP-1 and HWP-2 do not. The pumps are constant volume. This measure would modulate the pump speed. Traditionally, this measure would involve installing VFDs
1499 |  | Insulation and Air Sealing | Energy Savings | [7 empty] | Retrocommissioning | There are opportunities for insulation and air sealing in several locations. The bulkhead doors leading to the basement are leaky. Pipe insulation appeared to be good, but there were a few sections missing insulation. Lastly, the foundation walls appeared
1501 |  | Outside Airflow Reduction |  | 16000 | 15462 |  |  | 990 |  |  | MEP Cx | The project was completed in two stages. During the first stage, the AHU operated with a minimum outdoor air flow. During the second stage, and HRV was installed to provide OA to the AHU, but the OA damper was not closed and left at the position set at st
1502 |  | Replace Failed Equipment | Energy Savings | 2075 | 13000 | [5 empty] | Retrocommissioning
1502 |  | Fan Speed Modulation | Energy Savings | 19550 | 123700 | [5 empty] | Retrocommissioning
1502 |  | Rezone Classrooms | Energy Savings | 5550 | 35100 |  |  |  |  | 0 | Retrocommissioning
1526 |  | Outside Air AFMS | IAQ | [7 empty] | MEPBE Cx | The project design called for an airflow measuring station for measuring outside airflow for the 2 AHUs serving this building. During FPT, we found that these had never been installed because there wasn't enough straight run to install. However, this was
1549 |  | Miscellaneous Air Sealing | Energy Savings | 200 |  |  |  | 60 |  |  | MEP Cx | Miscellaneous air sealing opportunities of an already decent performing warehouse building. Measures included primary overhead and person door weather-stripping as well as select air sealing at the wall base.
1555 |  | Heat Pump Loop Heat Recovery | Energy Savings | 38235 | -270657 |  |  |  | 45375 |  | MEP Cx | Water-to-water heat pumps were installed to recovery heat from the hotel heat pump loop to use to provide heat for water park HRUs and water features. Benefits include reduced propane consumption for boilers and reduced cooling tower electricity consumpti
1569 |  | Bronch Exhaust not compliant in design documents | Code / Safety | [7 empty] | MEP Cx | During our design review, we brought up that the Bronch Exhaust didn't align with ASHRAE 170 requirements - ASHRAE 170-2017 6.3.2.2 defines that bronch exhaust shall discharge to the atmosphere in a vertical direction at least 10FT above adjoining roof le
1571 |  | Optimize RTU Supply Air Temperature Control | Energy Savings | 422 | 1497 |  |  | 383 |  |  | Retrocommissioning | According to the BAS graphics and the controls submittal, the supply air temperature setpoint for RTU-1 and RTU-2 is reset between 55°F and 65°F. The written sequence of operation from the controls submittal notes that the setpoint will be “reset automati
1571 |  | Optimize RTU Outdoor Air Control | Energy Savings | 447 | 2495 |  |  | 255 |  |  | Retrocommissioning | Currently RTU-1 and RTU-2 have minimum outside air damper positions of 10% and 30% respectively. Figure 11 and Figure 12 plot the outside air damper position vs. outdoor air temperature for RTU-1 and RTU-2. The OA damper for RTU-1 is commanded open to rel
1571 |  | Chilled Water Loop Differential Pressure Reset | Energy Savings | 105 | 950 |  |  | 0 |  | 0 | Retrocommissioning | The chilled water pump currently operates to maintain a fixed differential pressure setpoint in the chilled water loop. While this setpoint may be appropriate for periods when maximum cooling is required, the setpoint can be reset lower during part load c
1571 |  | Optimize Control of Hot Water Loop Pumps | Energy Savings | 111 | 1000 | [5 empty] | Retrocommissioning | Based on trend data analysis, the hot water loop pump appears to operate continuously 24/7 throughout the year (Figure 13). During unoccupied periods over the summer and shoulder seasons, it is unlikely that heat would be required at all times in the buil
1571 |  | Release BAS Overrides | Energy Savings; O&M | [7 empty] | Retrocommissioning | Occasionally, BAS overrides are put in place by facilities managers in order to temporarily solve a problem or address an issue and are left in place after the issue has been resolved. We only noticed one override in place – the minimum flow for VAV-3 was
1573 |  | Refrigeration Upgrade | Energy Savings | 5374 | 29854 | [5 empty] | Efficiency Consulting | Refrigeration Rack System Currently, the three walk-in coolers in the building are each served by a separate compressor, which rejects heat into the space where it is located. Installing a centralized refrigeration rack system would allow for the install
1573 |  | Implement Preventive Maintenance Plan | O&M | [7 empty] | Efficiency Consulting | The building walkthrough revealed numerous opportunities to improve building maintenance. Consider implementing a preventative maintenance (PM) plan. A PM plan gives the building owner a timeline of how often the equipment in the building should be re-vis
1573 |  | Replace Filters in AHUs | O&M | [7 empty] | Efficiency Consulting | One of the evident issues found during the building walkthrough was that filters were either very dirty, did not fit properly, or were not installed at all. We recommend replacing filters on a regular basis (every 3-6 months) to improve air quality and de
1573 |  | Automatic Variable Flow Kitchen Exhaust | Energy Savings | [7 empty] | Efficiency Consulting | The primary kitchen exhaust hood in the Kingdom Table kitchen has variable frequency drives (VFDs) on the fan motors, meaning the fan speed can modulate. However, the fan speed is controlled by a dial on the wall, which kitchen staff set at a certain spee
1573 |  | Energy Recovery Units | IAQ | [7 empty] | Efficiency Consulting | Ventilation to all the occupied spaces is critical for a healthy building and at the moment there is insufficient mechanical ventilation being brought into the building. We recommend installing an energy recovery unit for each tenant suite in the building
1578 |  | Summer Design Conditions | IAQ | [7 empty] | MEP Cx | We recommended adjusting the summer outdoor design conditions from 85F dry bulb/69F wet bulb to 90F dry bulb/74F wet bulb. Humidity levels had been brought up by the owner as a concern, and at the originally proposed design conditions, there was likelihoo
1594 |  | AII vs. Negative Pressure Rooms in Design | Code / Safety; IAQ; O&M | [7 empty] | MEP Cx | Original design had negative pressure rooms, but wouldn't satisfy Airborne Infection Isolation (AII) room requirements. When CxA brought this issue up during our first design review, the hospital indicated these should be AII and changes needed to be made
1594 |  | Exhaust fans proximity to AHUs OA intakes | Code / Safety | [7 empty] | MEP Cx | From the design review - Several Exhaust Fans were too close to the AHUs OA Intakes. ASHRAE 170 spells out requirements, but AII and ER Waiting Room exhaust is 25' horizontally, and also must be discharged 10' above roof. 30' from the discharge of AII EFs
1596 |  | Coil Piping Issues | O&M | [7 empty] | MEP Cx | Hot water and energy recovery coils were found to be piped differently than the design details. In addition, the design details didn't specify a required reverse return piping arrangement on multiple coil banks. We identified the piping issue and provid
1597 |  | Hot Water Pump Control | Energy Savings | [7 empty] | MEP Cx | The hot water distribution pumps for the boiler 1 and 2 heating loop were specified to enable any time the outside air temperatures were below 60F. This would have resulted in the pumps running many more hours of the year than needed, which increases both
1604 |  | Chiller vibration isolation | Code / Safety | [7 empty] | MEPBE Cx | From a PFC site visit, it was noted that the chiller which is located on the roof was mounted without vibration isolation (springs) which was required per the specifications. This could have resulted in potential vibration/sound issues. The contractor wil
1604 |  | Hot water pumps incorrect HP | O&M | [7 empty] | MEPBE Cx | From PFC - the installed hot water pumps were 1HP instead of 1.5HP per the design/submittal. This could have created potential capacity/flow issues once the building was occupied. The contractor has replaced these pumps with the correct ones.
1604 |  | Pump integration | O&M | [7 empty] | MEPBE Cx | The pumps had been submitted without bacnet cards even though they require integration. We recommended re-submitting w/bacnet
1607 |  | US Passive House (PHIUS) Equivalent Air Barrier | Energy Savings | [7 empty] | BE Cx | Commissioning efforts included installation verification visits, qualitative air barrier testing using theatrical fog, and compliance blower door testing and infrared imaging. The efforts of the BECx process helped yield blower door test results that met,
1611 |  | CHW Piping for greater chiller delta T | Energy Savings | [7 empty] | Retrocommissioning | We conducted an in depth review of the CHW plant and loads at SVMC. One outcome was that SVMC has acted on our recommendation to repipe a portion of the return which will increase the return water temps to the CHW plant. This wasn't a true RCx project but
1613 |  | Integrated Heat Pump Design | Energy Savings | 480 | 1790 |  |  | 785 |  |  | Efficiency Consulting | Replacing an R-22 split AC system with an ASHP with integrated controls for the boiler. Below 37F (economic balance point), the boiler operates, above 37F the Heat Pump operates
1620 |  | RTU Outside Air | Code / Safety | [7 empty] | MEP Cx | This project is the addition of a new MRI, making a new exam room and equipment room. The rooms need to follow ASHRAE 170 guidelines since it's a medical space. However, we found during submittal review that the RTU they spec'd did not have outside air at
1620 |  | Split AC Lineset Insulation Sealing | Energy Savings | [7 empty] | MEP Cx | We recommended sealing lineset insulation for outdoor refrigerant piping b/c we've seen pitting & leaks in copper piping from water getting beneath the insulation. This can lead to refrigerant leaks. 3 benefits - lower maintenance costs (don't need to rep
1632 |  | Slab Edge / Foundation Insulation | Energy Savings | 3150 | 2700 |  |  |  | 950 |  | BE Consulting / Diagnostics | Exterior infrared imaging revealed relatively significant conductivity around the perimeter of the building at the exposed slab edge/frost wall, as evidenced by the images below. This is not uncommon to see for foundation/slab systems that are uninsula
1632 |  | Overhead Door Replacement | Energy Savings | 7599 | 5000 |  |  |  | 2400 |  | BE Consulting / Diagnostics | Most overhead doors are uninsulated, likely due to the original nature of the building as an unconditioned space. The minimal R-value of the doors is established largely by the air films on either side of the door rather than the door itself. Additionally
1632 |  | Person Door Replacement | Energy Savings | 325 | 575 |  |  |  | 75 |  | BE Consulting / Diagnostics | Person swing doors typically exhibit a variety of conditions in which doors, hardware, and/or weather-stripping are damaged, rusted, or missing to varying degrees. While the total square footage of the swing doors is quite small, regarding the entirety of
1632 |  | Window Air Sealing | Energy Savings | 175 | 200 |  |  |  | 50 |  | BE Consulting / Diagnostics | The installed Pella window units likely are not installed in a manner that would satisfy manufacturer warranty requirements, and so Cx Associates assumes any warranties available are likely voided. However, they also do not appear to show any significant
1636 |  | AHU DAT Reset | Energy Savings | [7 empty] | MEPBE Cx | Multiple AHUs were specified to operate at constant 55F DAT. Supply air temperature reset was recommended and implemented.
1641 |  | Manufacturer Window Defect | O&M | 10000 | [6 empty] | BE Cx | Functional performance testing of the window units for water penetration identified a significant manufacturer defect across all window units. In-place repairs were made under warranty during system installation. Had this issue been identified post-constr
1643 |  | DOAS Unit Improved Integration | O&M | [7 empty] | Re-Commissioning | We'd commissioned the Lockwood Hotel when it was built, but during design they value-engineered out a ton of BAS integration. Sometime after our post-occ visit, one of the DOAS unit's cooling failed and the facilities staff had no idea for a long time (t
1645 |  | Existing RTU Ventilation | IAQ | [7 empty] | MEP Cx | This was a renovation project re-using some of the existing RTUs. The design included ventilation provided by the RTUs, but one of the existing units did not have OA or EA intakes. We brought this up to the owner and construction team so that the correct
1645 |  | Water Heater Strainer/Check Valve | O&M | [7 empty] | MEP Cx | The cold water piping entering the water heater was found to not have a strainer or check valve. These piping specialties protect the water heater against any debris in entering water that could result detrimental damage to the water heater. This could le
1646 |  | Insulate Exterior Walls | Energy Savings | 1580 |  |  |  | 1139 |  |  | BE Consulting / Diagnostics | Insulate currently uninsulated exterior walls to dramatically improve occupant comfort and reduce thermal heat loss and air leakage.
1647 |  | AHU Access | O&M | [7 empty] | MEP Cx | The coil pull space and some filter access for AHUs on this project were not adequate, and unfortunately this is how this was designed (we didn't do DR!). We asked the team to work with the manufacturer to determine how access could be handled with the s
1647 |  | Training Verification | O&M | [7 empty] | MEP Cx | We have training verification in our scope, so requested training plans from contractors. The mechanical contractor did not think they owed any training on newly installed equipment. Through close review of the specs, we found where training requirements
1649 |  | Unit Compartmentalization Cost Savings | First Cost | [7 empty] | MEPBE Cx | Identified an approach to apartment unit compartmentalization that ultimately provided better air tightness results than CM's prior approach and resulted in over a 50% cost savings, according to a verbal conversation with the CM. About $50,000 or a little
1658 |  | Building Envelope Improvement | Energy Savings | 1300 |  |  |  | 1073 |  |  | BE Consulting / Diagnostics | Redefining the envelope of a poorly air-sealed and moderately insulated attic floor by proposing it move to the plane of the roof slope, establishing an effective air and thermal barrier while also bringing all HVAC ductwork within the conditioned envelop
1705 |  | Infrared Findings | Energy Savings | [7 empty] | BE Consulting / Diagnostics | Multiple sources of air leakage were identified as a result of a qualitative infrared scan performed under negative building pressure. These leaks equate to operational energy costs if left unaddressed.
1774 |  | Decarbonization study to meet Carbon Risk Real Estate Monitor targets | Energy Savings | 104585.77 | 549118 |  |  |  |  | 203 | Retrocommissioning | Cx Associates was commissioned by Union Investment to conduct a decarbonization study for 600 13th Street in Washington, D.C. in order to move towards a climate neutral building
1793 |  | Estimated Energy Savings Based On Reduced Building Air Leakage Rate | O&M | 3000 | [6 empty] | MEPBE Cx | The goal for the Maine Medical Center Waldoboro Medical Office Building was to achieve the 2021 IECC air leakage rate target of 0.40 CFM/SF at 75 Pascals of pressure. Final blower door results show that the building was able to significantly exceed this t
1808 |  | Air Leakage Reduction | Energy Savings | 750 | [6 empty] | MEPBE Cx | Design review identified several improvement opportunities for air barrier continuity which were necessary in order to support the projects ambitious air tightness goal of 0.07 CFM75/SF. Code minimum is 0.25 CFM75/SF
Total | Sum |  |  | 936967.0755 | 3810813.7127 | 4110.74 | 1718.598 | 15081 | 78654.6795 | 508.774
| Count | 348
Confidential Information - Do Not Distribute
Copyright © 2000-2026 salesforce.com, inc. All rights reserved.